## Scoresheet
Air Force Sustainability Requirements Scoresheet
HPSB COMPLIANCE (Updated Jan 2017) |  |  |  | * required entry
General Information |  |  | INCOMPLETE
|  |  | Project ID (e.g. ABCD12345) | [5 empty] | SurveyData | *
|  |  | Real Property Unique ID (RPUID) | [5 empty] | SurveyData | *
|  |  | Facility Number | [5 empty] | SurveyData | *
|  |  | Building Name | [5 empty] | SurveyData | *
|  |  | Installation | [5 empty] | SurveyData | *
|  |  | City | [5 empty] | SurveyData
|  |  | State | [5 empty] | SurveyData
|  |  | CONUS | [5 empty] | SurveyData
|  |  | MAJCOM | [5 empty] | SurveyData
|  |  | Construction Agent | [5 empty] | SurveyData | *
SURVEY INCOMPLETE |  |  | AFCEC DM/CM (Last Name, First Name) | [5 empty] | SurveyData | *
|  |  | PA | [5 empty] | SurveyData | *
|  |  | Building Size (SF) | [5 empty] | SurveyData | *
|  |  | Program Year (FY####) | [5 empty] | SurveyData | *
|  |  | Project Phase | [5 empty] | SurveyData | *
|  |  | Design Started (MM/DD/YY) | [5 empty] | SurveyData | *
|  |  | BOD (MM/DD/YY) | [5 empty] | SurveyData | *
|  |  | Guiding Principles Compliance Certification Method | [5 empty] | SurveyData | *
|  |  | Date Project Registered (MM/DD/YY) | [5 empty] | SurveyData
|  |  | Date Project Certified (MM/DD/YY) | [5 empty] | SurveyData
|  | 0% | HPSB Compliant | [5 empty] | SurveyData
|  | 0% | Energy Efficiency Achieved (% below ANSI/ASHRAE/IESNA Standard 90.1-2013) | [5 empty] | SurveyData
|  | 2017-02-28 | Date Scoresheet Completed or Revised | [5 empty] | SurveyData
|  | 2017V1 | Scoresheet version | [5 empty] | SurveyData
Color Coding: See Instructions Tab for more detail
Drop-Down Box |  | Yes or N/A
No Entry Required |  | No
Custom Entry |  | Recommended not Required
90.1-2013
HPSB I: Employ Integrated Design Principles (UFC 1-200-02 para 2-2)
Total Points | 0 | INCOMPLETE | Possible Points | 2
| HPSB I.1 | Integrated Design |  | 1 | Federal Requirements | Integrated Design | HPSB I.1 |  |  | *
| HPSB I.2 | Commissioning |  | 1 | Federal Requirements | Commissioning | HPSB I.2 |  |  | *
HPSB II: Optimize Energy Performance (UFC 1-200-02 para 2-3)
Total Points | 0 | INCOMPLETE | Possible Points | 5
| HPSB II.1 | Energy Efficiency |  | 1 | Federal Requirements | Energy Efficiency
|  |  | Reduce energy use 30% below ANSI/ASHRAE/IESNA Standard 90.1-2013 or IECC, or if not - achieve maximum energy efficiency that is lifecycle cost effective |  | Federal Requirements | Energy Efficiency | HPSB II.1 |  |  | *
|  |  | Insert percentage below ANSI/ASHRAE/IESNA Standard 90.1-2013 or IECC, in terms of energy use (e.g. 32) |  | Federal Requirements | Energy Efficiency | HPSB II.1 |  |  | *
|  |  | Insert building energy intensity (kBtu/yr-sqft) calculated IAW 10 CFR 433 |  | Federal Requirements | Energy Efficiency | HPSB II.1 |  |  | *
|  |  | Roof Attributes (Recommended) |  | Federal Requirements | Energy Efficiency | HPSB II.1
|  |  | Select roof types (Check below) |  |  |  | HPSB II.1
HPSB II.1
|  | FALSE | Cool roof (LEED SS cr 7.2 or Energy Star) |  | Federal Requirements | Energy Efficiency | HPSB II.1
|  | FALSE | Green roof |  | Federal Requirements | Energy Efficiency | HPSB II.1
|  | FALSE | Solar electric |  | Federal Requirements | Energy Efficiency | HPSB II.1
|  | FALSE | Solar thermal |  | Federal Requirements | Energy Efficiency | HPSB II.1
|  | FALSE | Solar passive |  | Federal Requirements | Energy Efficiency | HPSB II.1
|  | Energy Efficient Products |  | 1
[5 empty] | Federal Requirements | Energy Efficient Products | HPSB II.1 |  |  | *
| HPSB II.2 | On-site Renewable Energy |  | 1 | Federal Requirements | On-site Renewable Energy | HPSB II.2
|  |  | Installed renewable energy elements or projects were not lifecycle cost effective |  | Federal Requirements | On-site Renewable Energy | HPSB II.2 |  |  | *
Renewable energy types (check below)
HPSB II.2
|  | FALSE | No Renewables |  | Federal Requirements | On-site Renewable Energy | HPSB II.2
|  | FALSE | Solar PV |  | Federal Requirements | On-site Renewable Energy | HPSB II.2
|  | FALSE | Solar CP |  | Federal Requirements | On-site Renewable Energy | HPSB II.2
|  | FALSE | Solar Thermal Electric |  | Federal Requirements | On-site Renewable Energy | HPSB II.2
|  | FALSE | Geothermal |  | Federal Requirements | On-site Renewable Energy | HPSB II.2
|  | FALSE | GSHP |  | Federal Requirements | On-site Renewable Energy | HPSB II.2
|  | FALSE | Wind |  | Federal Requirements | On-site Renewable Energy | HPSB II.2
|  | FALSE | Hydro |  | Federal Requirements | On-site Renewable Energy | HPSB II.2
|  | FALSE | WTE |  | Federal Requirements | On-site Renewable Energy | HPSB II.2
|  |  | Insert generation capacity (kW) |  | Federal Requirements | On-site Renewable Energy | HPSB II.2 |  |  | *
|  |  | Insert percentage of total building |  | Federal Requirements | On-site Renewable Energy |  |  |  | *
| HPSB II.3 | On-site Renewable Energy - Solar Hot Water Heater System |  | 1 | Federal Requirements | On-site Renewable Energy - Solar Hot Water Heater System | HPSB II.3
|  |  | Installed solar hot water heater system or found installation not lifecycle cost effective |  | Federal Requirements | On-site Renewable Energy - Solar Hot Water Heater System | HPSB II.3 |  |  | *
|  |  | Insert generation capacity (MMBtu/yr) |  | Federal Requirements | On-site Renewable Energy - Solar Hot Water Heater System | HPSB II.3 |  |  | *
|  |  | Insert percentage of demand |  | Federal Requirements | On-site Renewable Energy - Solar Hot Water Heater System | HPSB II.3 |  |  | *
| HPSB II.4 | Metering |  | 1 |  |  | HPSB II.4
|  |  | Electric Metering: Select N/A if no service |  | Federal Requirements | Metering | HPSB II.4 |  |  | *
|  |  | Natural Gas Metering: Select N/A if no service |  | Federal Requirements | Metering | HPSB II.4 |  |  | *
|  |  | Steam Metering: Select N/A if no service |  | Federal Requirements | Metering | HPSB II.4
HPSB III: Protect and Conserve Water (UFC 1-200-02 para 2-4)
Total Points | 0 | INCOMPLETE | Possible Points | 6
| HPSB III.1 | Indoor Water |  | 1 | Federal Requirements | Indoor Water | HPSB III.1 |  |  | *
|  | Indoor Water Metering |  | 1 | Federal Requirements | Indoor Water Metering | HPSB III.2 |  |  | *
| HPSB III.2 | Outdoor Water |  | 1 | Federal Requirements | Outdoor Water | HPSB III.2 |  |  | *
|  | Outdoor Water Metering |  | 1 | Federal Requirements | Outdoor Water Metering | HPSB III.3 |  |  | *
| HPSB III.3 | Alternative Water |  | 1 | Federal Requirements | Alternative Water | HPSB III.4 |  |  | *
| HPSB III.4 | Stormwater Management (LID Documentation per UFC 3-210-10) |  | 1
|  | No | Project is in the United States, US Territory, or Possession of the US |  | Federal Requirements | Storm Water Management | HPSB III.3
|  |  | Project includes construction or expansion of one or more buildings |  | Federal Requirements | Storm Water Management | HPSB III.3 |  |  | *
|  |  | Footprint is greater than 5,000 gross square feet |  | Federal Requirements | Storm Water Management | HPSB III.3 |  |  | *
|  |  | Change in Impervious Area (SF) |  | Federal Requirements | Storm Water Management | HPSB III.4 |  |  | *
|  |  | Pre-Award Cost Estimate ($) |  | Federal Requirements | Storm Water Management | HPSB III.4 |  |  | *
|  |  | Project addressed EISA 438 |  | Federal Requirements | Storm Water Management | HPSB III.4 |  |  | *
|  |  | EISA Technical Constraints |  | Federal Requirements | Storm Water Management | HPSB III.4
[5 empty] | Federal Requirements | Storm Water Management | HPSB III.4
|  | FALSE | Retaining stormwater on-site would adversely impact receiving water flows |  | Federal Requirements | Storm Water Management | HPSB III.3
|  |  | Site has shallow bedrock, contaminated soils, high groundwater table, underground facilities or utilities |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | Soil infiltration capacity is limited |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | Site is too small to infiltrate significant volume |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | Non-potable water demand (i.e. irrigation, toilets, & wash-water) is too small to warrant water harvesting and reuse system |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | Structural, plumbing, and other modifications to existing building to manage stormwater are infeasible |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | State or local regulations restrict water harvesting |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | State or local regulations restrict use of green infrastructure or LID |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | Other |  | Federal Requirements | Storm Water Management | HPSB III.3
|  |  | Percent Increase in Stormwater Runoff for 95 Percentile Storm (%) -or- Percent Increase in Stormwater Runoff from continuous simulation model, published data, studies, or other established tools (Reference UFC 3-210-10 Figure 2-1 Implementation of EISA Section 438) |  | Federal Requirements | Storm Water Management | HPSB III.4
|  |  | LID Features Locations |  | Federal Requirements | Storm Water Management | HPSB III.4
|  |  | Integrated Management Practices Employed |  | Federal Requirements | Storm Water Management | HPSB III.4
[5 empty] | Federal Requirements | Storm Water Management | HPSB III.4
|  | FALSE | Bio-Retention |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | Dry Wells |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | Filter Strips |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | Grassed Swales |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | Infiltration Trench |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | Inlet Pollution Removal Devices |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | Permeable Pavement / Pavers |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | Rain Barrels / Cisterns |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | Soil Amendments |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | Tree Box Filters |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | Vegetated Buffers |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | Vegetated Roof |  | Federal Requirements | Storm Water Management | HPSB III.3
|  | FALSE | Other |  | Federal Requirements | Storm Water Management | HPSB III.3
|  |  | Final LID Construction Cost ($) |  | Federal Requirements | Storm Water Management | HPSB III.4
|  |  | Post Construction Analysis (Name of DOR) |  | Federal Requirements | Storm Water Management | HPSB III.4
HPSB IV: Enhance Indoor Environmental Quality (UFC 1-200-02 para 2-5)
Total Points | 0 | INCOMPLETE | Possible Points | 8
| HPSB IV.1 | Thermal Comfort |  | 1 | Federal Requirements | Thermal Comfort | HPSB IV.1 |  |  | *
| HPSB IV.2 | Ventilation |  | 1 | Federal Requirements | Ventilation | HPSB IV.2 |  |  | *
| HPSB IV.3 | Daylighting |  | 1 | Federal Requirements | Moisture Control | HPSB IV.3 |  |  | *
| HPSB IV.4 | Moisture Control |  | 1 | Federal Requirements | Low Emitting Materials | HPSB IV.4 |  |  | *
| HPSB IV.5 | Low Emitting Materials |  | 1 | Federal Requirements | Low Emitting Materials | HPSB IV.5 |  |  | *
| HPSB IV.6 | Protect Indoor Air Quality during Construction |  | 1 | Federal Requirements | Protect Indoor Air Quality during Construction | HPSB IV.6 |  |  | *
| HPSB IV.7 | Environmental Tobacco Smoke Control |  | 1 | Federal Requirements | Environmental Tobacco Smoke Control | HPSB IV.7
| HPSB IV.8 | Occupant Health and Wellness |  | 1 | Federal Requirements | Occupant Health and Wellness | HPSB IV.8 |  |  | *
HPSB V: Reduce Environmental Impact of Materials (UFC 1-200-02 para 2-6)
Total Points | 0 | INCOMPLETE | Possible Points | 5
| HPSB V.1 | Recycled Content |  | 1 | Federal Requirements | Recycled Content | HPSB V.1 |  |  | *
| HPSB V.2 | Biologically-based Products |  | 1 | Federal Requirements | Biologically-based Products | HPSB V.2 |  |  | *
| HPSB V.3 | Ozone Depleting Substances |  | 1 | Federal Requirements | Ozone Depleting Substances | HPSB V.3
| HPSB V.4 | Waste and Materials Management - Recycling |  | 1 | Federal Requirements | Waste and Materials Management - Recycling | HPSB V.4 |  |  | *
0 | HPSB V.5 | Waste and Materials Management - Divert 60% from Disposal |  | 1
|  |  | 60% or greater diverted |  | Federal Requirements | Waste and Materials Management - Divert 60% from Disposal | HPSB V.5 |  |  | *
|  |  | Insert percentage diverted from landfill |  | Federal Requirements | Waste and Materials Management - Divert 60% from Disposal | HPSB V.5 |  |  | *
HPSB VI: Address Climate Change Risk (UFC 1-200-02 para 2-7)
Total Points | 0 | INCOMPLETE | Possible Points | 1
| HPSB VI.1 | Address Climate Change Risk |  | 1 | Federal Requirements | Address Climate Change Risk | HPSB VI.1 |  |  | *
|  |  | Possible Points | 27
0 | Federal Requirements - Yes or N/A | [6 empty] | SurveyResult
0 | Federal Requirements - No | [6 empty] | SurveyResult
0% | Percentage of Federal Requirements Met | [6 empty] | SurveyResult
Justification for Non-Applicable Answers
0 | HPSB I.1_NA | Integrated Design_NA |  |  | NA Justifications
0 | HPSB I.2_NA | Commissioning_NA |  |  | NA Justifications
0 | HPSB II.1_NA | Energy Efficiency_NA |  |  | NA Justifications
0 | HPSB II.1_NA | Energy Efficient Products_NA
0 | HPSB II.2_NA | On-site Renewable Energy_NA
0 | HPSB II.3_NA | On-site Renewable Energy - Solar Hot Water Heater System_NA
| HPSB II.4_NA | Metering_NA |  |  | NA Justifications
0 | HPSB II.4_NA_Electric | Electric Metering: Select N/A if no service_NA |  |  | NA Justifications
0 | HPSB II.4_NA_NaturalGas | Natural Gas Metering: Select N/A if no service_NA |  |  | NA Justifications
0 | HPSB II.4_NA_Steam | Steam Metering: Select N/A if no service_NA |  |  | NA Justifications
0 | HPSB III.1_NA | Indoor Water_NA |  |  | NA Justifications
0 | HPSB III.1_NA | Indoor Water Metering: Select N/A if no service_NA |  |  | NA Justifications
0 | HPSB III.2_NA | Outdoor Water_NA |  |  | NA Justifications
0 | HPSB III.2_NA | Outdoor Water Metering: Select N/A if no service_NA |  |  | NA Justifications
0 | HPSB III.3_NA | Alternative Water_NA
| HPSB III.4_NA | Stormwater Management_NA
0 | HPSB III.4_NA | Project addressed EISA 438_NA
0 | HPSB IV.1_NA | Thermal Comfort_NA |  |  | NA Justifications
0 | HPSB IV.2_NA | Ventilation_NA |  |  | NA Justifications
0 | HPSB IV.4_NA | Moisture Control_NA |  |  | NA Justifications
0 | HPSB IV.3_NA | Daylighting_NA |  |  | NA Justifications
0 | HPSB IV.5_NA | Low Emitting Materials_NA |  |  | NA Justifications
0 | HPSB IV.6_NA | Protect Indoor Air Quality during Construction_NA |  |  | NA Justifications
0 | HPSB V.1_NA | Recycled Content_NA |  |  | NA Justifications
0 | HPSB V.2_NA | Biologically based products_NA |  |  | NA Justifications
0 | HPSB V.3_NA | Ozone Depleting Substances_NA |  |  | NA Justifications
0 | HPSB V.4_NA | Waste and Materials Management - Recycling_NA |  |  | NA Justifications
0 | HPSB V.5_NA | Waste and Materials Management - Divert 60% from Disposal_NA |  |  | NA Justifications
0 | HPSB VI.1_NA | Address Climate Change Risk_NA
Note on D92: HPSB III.3 Stormwater Management is required if: Project is in the United States, US Territory, or Possession of the US; Project includes construction or expansion of one or more buildings; AND Footprint (new impervious surfaces) is greater than 5,000 gross square feet.
Solar PV
Solar CP
Solar Thermal Electric
Geothermal
GSHP
Wind
Hydro
Waste to Energy
Renewables were not lifecycle cost effective
Date Project Registered (MM/DD/YY)
Date Project Certified (MM/DD/YY)
Clear
Cool roof
Green roof
Solar electric
Solar thermal
Solar Passive
Retaining stormwater impact receving water flow
Site too small to infiltrate significant volume
State or local restrict water harvesting
Shallow bedrock, contaminated soil, high ground water table, underground utilities
Non-potable water demand to small
Structural, plumbing, and other mods not feasible
Soil infiltration capacity limited
State or local restrict use of green infrastructure or LID
Other
Bio-Retention
Infiltration Trench
Soil Amendments
Dry Wells
Inlet Pollution Removal Device
Permeable Pavement/Pavers
Filter Strips
Grassed Swells
Rain Barrels/Cisterns
Tree Box Filters
Vegetated Buffers
Vegetated Roof
Other

## NA_Justification
Federal Requirements for High Performance and Sustainable Buildings (HPSB) & UFC 1-200-02
Instructions: Provide a common or project specific justification for an element to be non-applicable, when completed, the Scoresheet tab will allow an N/A response.
Justification for Non-Applicable Answers |  | Common Justification | Project Specific Justification | Complete?
HPSB I: Employ Integrated Design Principles (UFC 1-200-02, 2-2)
HPSB I.1 | Integrated Design |  |  | Applicable
HPSB I.2 | Commissioning |  |  | Applicable
HPSB II: Optimize Energy Performance (UFC 1-200-02, 2-3)
HPSB II.1 | Energy Efficiency |  |  | Applicable
HPSB II.1 | Energy Efficient Products |  |  | Applicable
HPSB II.2 | On-site Renewable Energy |  |  | Applicable
HPSB II.3 | On-site Renewable Energy - Solar Hot Water Heater System |  |  | Applicable
HPSB II.4 | Metering
HPSB II.4 | Electric Metering: Select N/A if no service |  |  | Applicable
HPSB II.4 | Natural Gas Metering: Select N/A if no service |  |  | Applicable
HPSB II.4 | Steam Metering: Select N/A if no service |  |  | Applicable
HPSB III: Protect and Conserve Water (UFC 1-200-02, 2-4)
HPSB III.1 | Indoor Water |  |  | Applicable
HPSB III.1 | Indoor Water Metering: Select N/A if no service |  |  | Applicable
HPSB III.2 | Outdoor Water |  |  | Applicable
HPSB III.2 | Outdoor Water Metering: Select N/A if no service |  |  | Applicable
HPSB III.3 | Alternative Water |  |  | Applicable
HPSB III.4 | Stormwater Management
HPSB III.4 | Project addressed EISA 438 |  |  | Applicable
HPSB III.4 |  |  |  | Applicable
HPSB III.4 |  |  |  | Applicable
HPSB IV: Enhance Indoor Environmental Quality (UFC 1-200-02, 2-5)
HPSB IV.1 | Thermal Comfort |  |  | Applicable
HPSB IV.2 | Ventilation |  |  | Applicable
HPSB IV.3 | Daylighting |  |  | Applicable
HPSB IV.4 | Moisture Control |  |  | Applicable
HPSB IV.5 | Low Emitting Materials |  |  | Applicable
HPSB IV.6 | Protect Indoor Air Quality during Construction |  |  | Applicable
HPSB IV.8 | Occupant Health and Wellness |  |  | Applicable
HPSB V: Reduce Environmental Impact of Materials (UFC 1-200-02, 2-6)
HPSB V.1 | Recycled Content |  |  | Applicable
HPSB V.2 | Biologically based products |  |  | Applicable
HPSB V.3 | Ozone Depleting Substances |  |  | Applicable
HPSB V.4 | Waste and Materials Management - Recycling |  |  | Applicable
HPSB V.5 | Waste and Materials Management - Divert 60% from Disposal |  |  | Applicable
HPSB VI: Adress Climate Change Riskd (UFC 1-200-02, 2-7)
HPSB VI.1 | Address Climate Change Risk |  |  | Applicable

## Guidance
High Performance Sustainable Building Requirements
References
Executive Order (EO) 13693, Planning for Federal Sustainability in the Next Decade
HPSB I: Employ Integrated Design Principles
Integrated Design HPSB I.1 UFC 1-200-02 para 2-2.1 | Incorporate the following planning and evaluation into the integrated design, as described in ASHRAE 189.1 Informative Appendix F (Integrated Design). Follow the steps of design optimization, as applicable, in ASHRAE 189.1 Section F1.1.1 (Charrette Process). Use a collaborative, integrated planning and design team, composed of user, government support staff, and appropriate professionals, to identify requirements and to establish performance goals for siting, energy, water, materials, indoor environmental quality, and other comprehensive design goals. Ensure incorporation of these goals throughout the design and lifecycle of the building, including deconstruction. Evaluate the site and building components to determine whether passive and natural design strategies and features are cost effectively incorporated before the active and mechanical systems are designed. Incorporate these features where applicable. Take into account site attributes, including climate and local and regional context, which impact the design of the building. During the site selection process, meet the requirements of UFC 2-100-01. See Appendix B “Best Practices” for desirable site characteristics. During the planning and design process meet the requirements of applicable UFCs, and use the following site development considerations and passive strategies: • Site design elements that ensure safe and convenient pedestrian access. • Meet the requirements of UFC 3-201-02. • Incorporate results of site analysis, in order to design the building, focusing on orientation, configuration and massing. • Orient building to maximize energy efficiency, passive solar and daylighting potential. • Select, design and integrate into the overall building, high performance and sustainable systems (e.g., HVAC, plumbing, water heating systems, lighting systems, control systems, elevators, building envelope and fire protection systems). • Promote opportunities for occupants to voluntarily increase physical movement such as making stairwells a desirable option for circulation and active workstations.
Commissioning HPSB I.2 UFC 1-200-02 para 2-2.2 | In order to verify design and performance, and ensure that the Government requirements are met, employ commissioning practices appropriate to the size and complexity of the building and its system components. This must include an experienced commissioning provider, who should be independent of the project design and construction team, and the operations team. The choice of either contracted services or Government personnel to serve as the commissioning provider will be determined at project level. Meet the requirements of ASHRAE 189.1 Section 10.3.1.2 (Building Project Commissioning), with the following modifications: • For buildings and systems that are less complex6, commissioning may be tailored as determined by the DOD Component AHJ. • “Schematic design” is the design charrette or similar conceptual design activity. • Documentation as described in ASHRAE 55 Section 6.2 is not required. For Air Force projects, the Project Delivery Team must determine the level of commissioning activities required.
Requirement Source Document(s) | Executive Order 13693
UFGS 01 91 00.15, Total Building Commissioning
HPSB II: Optimize Energy Performance
Energy Efficiency HPSB II.1 UFC 1-200-02 para 2-3.1 | Energy Efficiency - Base energy efficiency design decisions on life-cycle cost as indicated in Chapter 1 of UFC 1-200-02. Commercial and Multi-Family High-Rise Residential Buildings: • Meet the requirements of ASHRAE 90.1. Use ASHRAE 90.1(2010) for all projects with design starts before November 6, 2016. Use ASHRAE 90.1(2013) thereafter. • Design the building to achieve at least 30% energy consumption reduction from ASHRAE 90.1 baseline. • If a 30% reduction is not LCCE, modify the design of the proposed building to achieve an energy consumption level at the highest level of energy efficiency that is LCCE. • Determine energy consumption levels for both the ASHRAE Baseline Building and proposed building by using the Performance Rating Method found in appendix G of ASHRAE 90.1, except the formula for calculating the Performance Rating. Replace the formula in G1.2 with the following: Percentage improvement = 100 × ((Baseline building consumption − Receptacle and process loads) − (Proposed building consumption − Receptacle and process loads)) / (Baseline building consumption − Receptacle and process loads) Low-Rise Residential Buildings: • Meet the requirements of International Energy Conservation Code (IECC). • Design the building to achieve at least 30% energy consumption reduction from the IECC baseline using the Simulated Performance Alternative found in Section 405 of the IECC. • If a 30% reduction is not LCCE, modify the design of the proposed building to achieve an energy consumption level at the highest level of energy efficiency that is LCCE. Renovations: • Renovation projects that replace everything above the foundation must either apply 2-3.1.1 or 2-3.1.2 as applicable. • All other renovations choose one of the following options: 1. Reduce measured building energy use by at least 30%, below FY 2003 energy use baseline. 2. Reduce measured building energy use by at least 20% below FY 2015 energy use baseline. 3. Reduce modeled energy use (from all sources including renewable energy) by 20% compared to the ASRHAE 90.1 baseline building design. • If none of the reduction choices is life-cycle cost-effective, modify the design of the proposed building system(s) to achieve an energy consumption level at the highest level of energy efficiency that is life-cycle cost-effective.
Energy Efficient Products HPSB II.1 UFC 1-200-02 para 2-3.1.4 | Energy Efficient Products – Per EISA 2007 Section 525, acquire products that are ENERGY STAR®-qualified or meet FEMP-designated efficiency requirements in all covered product categories. Select products based on life cycle cost, not initial cost. Link to EPA sites: http://www.energystar.gov/ or http://www1.eere.energy.gov/femp/ Per EISA 2007 Section 524, provide commercially available, off-the-shelf products that use no more than 1 watt in their standby mode.
Requirement Source Document(s) | 10 CFR 433, EPAct 05
Links | Energy Star®
Federal Energy Management Program
On-site Renewable Energy HPSB II.2 UFC 3-440-01 para 2-3.2 | Provide on-site renewable energy systems in accordance with ASHRAE 189.1 Section 7.4.1.1 (On-Site Renewable Energy Systems) and UFC 3-440-01 where LCCE, considering climate, infrastructure condition, mission compatibility, and effects on base wide electrical system (grid) power quality. Exception: Do not use purchase of renewable energy certificates (RECs) as a substitute for the Section 7.4.1.1 new building requirement. Air Force will utilize an installation-level solution to renewable energy systems and will not require ASHRAE 189.1 Section 7.3.2 if a building-level solution is not LCCE.
Requirement Source Document(s): | Executive Order 13693
On-Site Renewable Energy – Solar Hot Water Heater System HPSB II.3 UFC 1-200-02 para 2-3.2.1 | Per EISA 2007 Section 523, meet at least 30% of the annual domestic hot water requirement through the installation of solar water heating unless SDHW is not LCCE. If 30% is not LCCE, modify the design of the proposed system to achieve the highest level of solar water heating that is LCCE.
Requirement Source Document(s):
Measurement and Verification HPSB II.4 UFC 1-200-02 para 2-3.4 | A utility meter must be installed at each building, for each utility serving the building (e.g., district steam, district hot and chilled water, electricity, natural gas, fuel oil, etc.) in the standard units of the measure. Meters must be connected to a base wide energy and utility monitoring and control system using the installation’s advanced metering protocols. The installation of meters is required per DODI 4170.11, and as amended by DOD Utilities Meter Policy, 16 April 2013.
Requirement Source Document(s): | EPAct 2005 Section 103, EISA 2007 Section 434
Links | Energy Policy Act of 2005
UFC 2-4.3: Provide an Energy Compliance Analysis (Recommended) | Provide an Energy Compliance Analysis (ECA) which will demonstrate compliance with all energy related requirements in this UFC.
UFC Reference | UFC 1-200-02, 2-4.3
LEED Credit(s) aligns closely with HPSB: | None
LEED Credit(s) meet HPSB: | None
Energy Efficiency HPSB II.1 UFC 1-200-02 para 2-3.1 | For new Federal buildings and Federal buildings undergoing major renovations…(I) The buildings shall be designed so that the fossil fuel generated energy consumption of the buildings is reduced, as compared with such energy consumption by a similar building in fiscal year 2003 (CBECS or RECS data from EIA), by the percentage specified...FY2010 (55%), 2015 (65%), 2020 (80%), 2025 (90%), and 2030 (100%). The DOE Rulemaking is not yet complete
Requirement Source Document(s): | EISA 2007, Sec. 433, (a)(D)(i)
Links | Energy Independence and Security Act of 2007
LEED Credit(s) aligns closely with HPSB: | None
LEED Credit(s) meet HPSB: | None
HPSB 2.6: Benchmarking | Compare annual performance data with previous years’ performance data, by entering annual performance data in a measurement and tracking tool such as EPA’s ENERGY STAR®, Portfolio Manager. The Labs21® Energy Benchmarking Tool may be used to benchmark laboratory buildings. Results of benchmarking should be used to inform capital investment decisions for future projects.
UFC Reference | UFC 1-200-02, 2-4.5
Requirement Source Document(s): | Federal Leadership in High Performance and Sustainable Buildings MOU
HPSB III: Protect and Conserve Water
Indoor Water HPSB III.1 UFC 1-200-02 para 2-4.1 | Indoor Water – Base water efficiency design decisions on life-cycle cost as indicated in Chapter 1 of UFC 1-200-02. • Meet the requirements of ASHRAE 189.1 Section 6.3.2 (Building Water Use Reduction), which incorporates USEPA WaterSense-labeled products. Water closet replacements in renovations may have a flush value of up to 1.6 GPF (6.1 LPF) to accommodate existing plumbing capacity. • Meet the requirements of ASHRAE 189.1 Section 6.4.2 (Building Water Use Reduction). • Meet the requirements of ASHRAE 189.1 Section 6.4.3 (Special Water Features).
Indoor Water Metering HPSB III.1 UFC 1-200-02 para 2-4.1.1 | Indoor Water Metering -- Install advanced water meters to monitor building indoor potable water consumption, as required by DOD Utilities Meter Policy, 16 April 2013.
Requirement Source Document(s): | EPAct 1992
Outdoor Water HPSB III.2 UFC 1-200-02 para 2-4.2 | Outdoor Water -- • Limit potable irrigation water use by 50% compared to the conventional methods, and when LCCE, by using the methodologies in ASHRAE 189.1: Section 6.3.1 (Mandatory Provisions: Site Water Use Reduction) and either Section 6.4.1 (Prescriptive Option: Site Water Use Reduction) or Section 6.5.1 (Performance Option: Site Water Use Reduction). • For existing systems, if a building has a single water meter, reduce indoor and outdoor potable water use combined by at least 20% compared to building water use in 2007. Compare results to a baseline building, using the EPA WaterSense landscape water budget tool version 1.01 or later, or a Component approved tool. • Show preference for irrigation contractors who are certified through a WaterSense labeled program, or other industry-recognized credentialing programs. • Refer to UFC 3-201-02 for additional requirements.
Outdoor Water MeteringWater HPSB III.2 UFC 1-200-02 para 2-4.2.1 | Water metering for landscaping – When potable water is used, provide water meters for irrigation systems serving more than 25,000 square feet of landscape, when life-cycle cost-effective. Install advanced water meters to monitor outdoor potable water consumption, as required by DOD Utilities Meter Policy, 16 April 2013. For all other irrigation systems, separate water meters for locations with outdoor water use are encouraged.
Requirement Source Document(s): | Executive Order 13693
Alternative Water HPSB III.3 UFC 1-200-02 para 2-4.3 | Where life-cycle cost-effective and permitted by local laws and regulations, use alternative water sources, such as harvested rainwater, treated wastewater, air handler condensate capture, grey water, and reclaimed water.
Requirement Source Document(s):
Stormwater Management HPSB III.4 UFC 3-210-10 para 2-4.3.1 | The criteria and design standards in UFC 3-210-10 are required for the planning, design and construction of all Department of Defense (DoD) projects in the United States, United States Territories and Possessions of the United States that meet both of the following conditions: 1) The project includes construction or expansion of one or more buildings as part of its primary scope (i.e., primary facilities vice supporting facilities). 2) The “footprint” is greater than 5,000 gross square feet (464.5 square meters). “Footprint” consists of all new impervious surfaces associated with the building(s), including both building area and pavement area of associated supporting facilities (such as parking and sidewalks). “Footprint” does not include existing building area to be renovated, existing pavement area to be resurfaced, or new pavement area other than supporting facilities associated with the building(s). For projects in the United States, United States Territories, and Possessions of the United States that do not meet the applicability requirements above, LID techniques apply to the extent practical.
Requirement Source Document(s): | EISA 2007 Sec 438
HPSB IV: Enhance Indoor Environmental Quality
Thermal Comfort HPSB IV.1 UFC 1-200-02 para 2-5.1 | Meet the requirements of ASHRAE 55. Compliance with standards by providing passive (non-mechanical) thermal comfort methods are allowed and encouraged as described in paragraph entitled, “Integrated Design” in UFC 1-200-02. Exception: For Medical Treatment Facilities, refer to UFC 4-510-01 Medical Military Facilities for thermal comfort criteria.
Requirement Source Document(s): | Executive Order 13693
Ventilation HPSB IV.2 UFC 1-200-02 para 2-5.1 | Meet the requirements of ASHRAE 62.1 (62.2 for low-rise residential). Exception: For Medical Treatment Facilities, refer to UFC 4-510-01 Medical Military Facilities for ventilation criteria.
Requirement Source Document(s): | Executive Order 13693
Daylighting HPSB IV.3 UFC 1-200-02 para 2-5.2 | All regularly occupied spaces located on the exterior wall must have vision fenestration. Where mission precludes vision fenestration for regularly occupied spaces located on the exterior wall, daylighting is still required. All classrooms and offices must have daylighting. Meet the requirements of ASHRAE 189.1 Section 8.4.1.2 (Minimum Sidelighting effective Aperture for Office Spaces and Classrooms) or Section 8.5.1.2 (Usable Daylight Illuminance in Office Spaces and Classrooms). Provide automated lighting controls in accordance with UFC 3-530-01. Exception: For Medical Treatment Facilities, refer to UFC 4-510-01 Medical Military Facilities for additional daylighting criteria.
Requirement Source Document(s): | Executive Order 13693
Moisture Control HPSB IV.4 UFC 1-200-02 para 2-5.3.1 | Establish and implement a moisture control strategy for controlling moisture flows and condensation to prevent building damage, minimize mold contamination, and reduce health risks related to moisture. Meet the requirements of ASHRAE 189.1 Section 10.3.1.5 (Moisture Control), UFC 3-410-01, Chapter 3, Sections 3-2 and 3-3 (Ventilation Air), and UFC 3-101-01 Chapter 3 (Building Envelope Requirements). Refer to Appendix B “Protect Indoor Air Quality” for best practices.
Requirement Source Document(s): | Executive Order 13693
Low Emitting Materials HPSB IV.5 UFC 1-200-02 para 2-5.3.2 | Specify materials and products with low or no pollutant emissions, including composite wood products, adhesives, sealants, interior paints and finishes, carpet systems, and furnishings. Meet the requirements of ASHRAE 189.1 Section 8.4.2 (Prescriptive Option: Materials). Exception: Exclude compliance with 8.4.2, first sentence.
Requirement Source Document(s): | Executive Order 13693
Protect Indoor Air Quality during Construction HPSB IV.6 UFC 1-200-02 para 2-5.3.3 | For new construction and for renovation of unoccupied existing buildings, comply with ASHRAE 189.1 Section 10.3.1.4 (Indoor Air Quality (IAQ) Construction Management), with maximum outdoor air consistent with achieving relative humidity no greater than 60%. For renovation of occupied existing buildings, comply with ANSI/SMACNA 008-2008, 2nd Edition, SMACNA IAQ Guidelines for Occupied Buildings Under Construction.
Requirement Source Document(s): | Executive Order 13693
Environmental Tobacco Smoke Control HPSB IV.7 UFC 1-200-02 para 2-5.3.4 | Prohibit smoking within the building and within a minimum of 50 feet (15.24 meters) of all building entrances, operable windows, and building ventilation intakes. Verify if more stringent facility criteria or Installation policy applies.
Requirement Source Document(s): | Federal Register: December 22, 2008 (Volume 73, Number 246) - EO 13058
Occupant Health and Wellness HPSB IV.8 UFC 1-200-02 para 2-5.4 | Promote opportunities for occupants to voluntarily increase physical movement such as making stairwells a desirable option for circulation, active workstations, fitness centers, and bicycle commuter facilities. Support occupant health by considering options such as providing convenient access to healthy dining options, potable water, daylight, plants, and exterior views. Indicate in the Integrated Design Process how these efforts were evaluated.
Requirement Source Document(s):
HPSB V: Reduce Environmental Impact of Materials
Recycled Content HPSB V.1 UFC 1-200-02 para 2-6.1.1 | Use RCRA Section 6002 compliant products that meet or exceed EPA's recycled content recommendations, available on EPA’s Comprehensive Procurement Guideline web site at http://www.epa.gov/
Requirement Source Document(s): | RCRA 2002, Sec 6002
Biologically-based Products HPSB V.2 UFC 1-200-02 para 2-6.1.2 | Per Section 9002 of the Farm Security and Rural Investment Act, specify products composed of the highest percentage of biobased content consistent with the USDA BioPreferred Program, if products meet performance requirements and are available at a reasonable cost. Exceptions taken to biobased product procurement must be documented. A preference for purchasing products with the highest biobased content per USDA recommendations for designated product categories must be included in all applicable solicitations. USDA’s biobased product designations and biobased content (which includes certified sustainably-harvested and rapidly renewable resources) recommendations are available on USDA’s BioPreferred web site at http://www.biopreferred.gov/
Requirement Source Document(s): | FSRIA 2002 Section 9002
Environmentally Preferable Products HPSB V.3 UFC 1-200-02 para 2-6.1.4 | Meet the requirements of ASHRAE 189.1 Section 9.3.3 (Refrigerants), if equipment or systems using ozone depleting substances are included in the project. Do not use ozone depleting substances (ODS) or high Global Warming Potential (GWP) chemicals where EPAs Significant New Alternative Policy (SNAP) has identified acceptable substitutes or where other environmentally preferable products are available for use in construction, repair or end-of-life replacements: www.epa.gov/snap Exceptions: Refer to UFC 3-600-01 for fire protection system requirements.
Requirement Source Document(s): | Executive Order 13693
Waste and Materials Management - Recycling HPSB V.4 UFC 1-200-02 para 2-6.2.1 | Meet the requirements of ASHRAE 189.1 Section 9.3.4.1 (Storage and Collection of Recyclables – Recyclables), where markets or onsite recycling exist.
Requirement Source Document(s): | Executive Order 13693
Waste and Materials Management, Divert 60% from Disposal HPSB V.5 UFC 1-200-02 para 2-6.2.2 | Divert minimum 60% of nonhazardous construction and demolition waste material from landfills.
Requirement Source Document(s): | Executive Order 13693
UFGS 01 74 19, Construction and Demolition Waste Management
HPSB VI: Adress Climate Change Risk
Address Climate Change Risk HPSB VI.1 UFC 1-200-02 para 2-7 | Provide building design solutions responsive to any Government-provided projections of climate change projection and determination of acceptable risk. For a building located in a floodplain of concern, provide design solutions which mitigate both impact on the floodplain, and impact of the design flood event on building function and occupants, consistent with mission criticality.

## Color Legend
AF Sustainable Building Requirements Legend
Gray Text | Recommended (Federal Requirement not fully defined at this time)
Light Gray Cell | Cell is populated by other cells. User is not required to enter values.
Light Green Cell (When used, conditional formatting changes cell to Green or Red depending on entry) | Cell provides a drop-down box for the user to select which LEED Credits and HPSB Requirements that the project is attempting. When a "Yes" or "No" is selected the cell follows the stoplight convention to visually represent progress. The stoplight convention is also used for "Yes" or "No" totals. Some light green boxes also have an option for "N/A" when used for subquestions
Cell uses a drop down box and user is designating "Yes" or "N/A" when applicable
Cell uses a drop down box and user is designating "No"
Light Yellow Cell | Cell is for custom entry on how the project is pursuing HPSB requirements. These are subquestions and also general information questions. Boxes that appear when cell is selected give further instruction on entering data. Some cells restrict values that can be entered - which is explained if incorrectly entered

## LocationList (hidden)
****FOUO******
BASE Selections:
BASE NAME | CITY | STATE | CONUS | MAJCOM
Altus AFB | Altus | OK | Yes | AETC
Arnold AFB | Manchester | TN | Yes | AFMC | Andersen AFB | Agana | Guam | No | PACAF
Aviano AB | Pordenone | Italy | No | USAFE | Joint Region Marianas-Guam-Andersen
Barksdale AFB | Bossier City | LA | Yes | AFGSC
Beale AFB | Yuba City | CA | Yes | ACC
Bellows AFB | Honolulu | HI | Yes | PACAF
Buckley AFB | Denver | CO | Yes | AFSPC
Cannon AFB | Clovis | NM | Yes | AFSOC
Cape Canaveral AFS | Cape Canaveral | FL | Yes | AFSPC
Cheyenne Mountain AFS | Colorado Springs | CO | Yes | AFSPC
Columbus AFB | Columbus | MS | Yes | AETC
Creech AFB | Indian Springs | NV | Yes | ACC
Davis-Monthan AFB | Tucson | AZ | Yes | ACC
Dover AFB | Dover | DE | Yes | AMC
Dyess AFB | Abilene | TX | Yes | ACC
Edwards AFB | Edwards AFB | CA | Yes | AFMC
Eglin AFB | Valpariso | FL | Yes | AFMC
Eielson AFB | Fairbanks | AK | Yes | PACAF
Ellsworth AFB | Rapid City | SD | Yes | ACC
F. E. Warren AFB | Cheyenne | WY | Yes | AFGSC
Fairchild AFB | Spokane | WA | Yes | AMC
Goodfellow AFB | San Angelo | TX | Yes | AETC
Grand Forks AFB | Grand Forks | ND | Yes | AMC
Hanscom AFB | Bedford | MA | Yes | AFMC
Hill AFB | Ogden | UT | Yes | AFMC
Holloman AFB | Alamogordo | NM | Yes | ACC
Hurlburt Field | Ft Walton Beach | FL | Yes | AFSOC
Incirlik AB | Incirlik | Turkey | No | USAFE
Izmir | Izmir | Turkey | No | USAFE
Joint Base Anacostia-Bolling | Washington DC | DC | Yes | AFDW
Joint Base Andrews | Camp Springs | MD | Yes | AFDW
Joint Base Cape Cod | Bourne | MA | Yes | AFSPC
Joint Base Charleston | Charleston | SC | Yes | AMC
Joint Base Elmendorf-Richardson | Anchorage | AK | Yes | PACAF
Joint Base Langley-Eustis | Hampton | VA | Yes | ACC
Joint Base Lewis-McChord AFB | Tacoma | WA | Yes | AMC
Joint Base McGuire-Dix-Lakehurst | Trenton | NJ | Yes | AMC
Joint Base Myer-Henderson Hall |  | VA | Yes
Joint Base Pearl Harbor-Hickam | Honolulu | HI | Yes | PACAF
Joint Base San Antonio - Fort Sam Houston | San Antonio | TX | Yes | AETC
Joint Base San Antonio - Lackland | San Antonio | TX | Yes | AETC
Joint Base San Antonio - Randolph | San Antonio | TX | Yes | AETC
Joint Expeditionary Base Little Creek-Fort Story |  | VA | Yes
Joint Region Marianas-Guam-Andersen | Guam | Guam | No
Kadena AB | Okinawa | Japan | No | PACAF
Keesler AFB | Biloxi | MS | Yes | AETC
Kirtland AFB | Albuquerque | NM | Yes | AFMC
Kunsan AB | Kunsan City | S. Korea | No | PACAF
Lajes Field | Terceira Island | Puerto Rico | No | USAFE
Laughlin AFB | Del Rio | TX | Yes | AETC
Little Rock AFB | Little Rock | AR | Yes | AMC
Los Angeles AFB | El Segundo | CA | Yes | AFSPC
Luke AFB | Phoenix | AZ | Yes | AETC
MacDill AFB | Tampa | FL | Yes | AMC
Malmstrom AFB | Great Falls | MT | Yes | AFGSC
Maxwell-Gunter AFB | Montgomery | AL | Yes | AETC
McConnell AFB | Wichita | KS | Yes | AMC
Minot AFB | Minot | ND | Yes | AFGSC
Misawa AB | Misawa | Japan | No | PACAF
Moody AFB | Valdosta | GA | Yes | ACC
Mountain Home AFB | Mountain Home | ID | Yes | ACC
Nellis AFB | Las Vegas | NV | Yes | ACC
Offutt AFB | Bellevue | NE | Yes | ACC
Osan AB | Osan | S. Korea | No | PACAF
Other | Other | Other | Other
Patrick AFB | Cocoa Beach | FL | Yes | AFSPC
Peterson AFB | Colorado Springs | CO | Yes | AFSPC
Pope AFB | Fayetteville | NC | Yes
RAF Alconbury | Alconbury | United Kingdom | No | USAFE
RAF Croughton | Croughton | United Kingdom | No | USAFE
RAF Fairford | Fairford | United Kingdom | No | USAFE
RAF Lakenheath | Lakenheath | United Kingdom | No | USAFE
RAF Mildenhall | Mildenhall | United Kingdom | No | USAFE
Ramstein AB | Kaiserslautern | Germany | No | USAFE
Robins AFB | Warner Robins | GA | Yes | AFMC
Rome Laboratory | Rome | NY | Yes | AFMC
Schriever AFB | Colorado Springs | CO | Yes | AFSPC
Scott AFB | Bellville | IL | Yes | AMC
Seymour Johnson AFB | Goldsboro | NC | Yes | ACC
Shaw AFB | Sumter | SC | Yes | ACC
Sheppard AFB | Witchita Falls | TX | Yes | AETC
Spangdahlem AB | Trier | Germany | No | USAFE
Thule AB | Thule | Greenland | No | AFSPC
Tinker AFB | Oklahoma City | OK | Yes | AFMC
Travis AFB | Fairfield | CA | Yes | AMC
Tyndall AFB | Panama City | FL | Yes | ACC
USAF Academy | Colorado Springs | CO | Yes | USAFA
Vance AFB | Enid | OK | Yes | AETC
Vandenberg AFB | Lompoc | CA | Yes | AFSPC
Whiteman AFB | Knob Noster | MO | Yes | AFGSC
Wright-Patterson AFB | Dayton | OH | Yes | AFMC
Yokota AB | Tokyo | Japan | No | PACAF

## Dropdowns (hidden)
Date Test | Greater Than FY | Dsg Start
90.1-2013 | 2015 | 2016-11-06
Key for Saving VBA code | Incomplete
Completeness Check | 0
General Information | INCOMPLETE
HPSB 1 - Integrated Design | INCOMPLETE
HPSB 2 - Energy | INCOMPLETE
HPSB 3 - Water | INCOMPLETE
HPSB 4 - IAQ | INCOMPLETE
HPSB 5 - Materials | INCOMPLETE
HPSB 6 - Climate | INCOMPLETE
NA Check | 0
Incomplete
NA Defaults
NA LCCE | Yes
NA Mission Restriction | Yes
NA Location/Regional Restriction | Yes
NA Locale Restriction | Yes