## MSM
Building - West
h1 - Height of Pole Mast (ft): | 70
h2 - Height of Structure (ft): | 43
D - Coverage-Horizontal distance (ft): | 13.2295
Building size (width) (ft) | 48.5
Building side cover (ft) | 12.125
Building - South
h1 - Height of Pole Mast (ft): | 70
h2 - Height of Structure (ft): | 43.5
D - Coverage-Horizontal distance (ft): | 12.8848
SIDEFLASH - At Midpoint of Catenary (Lowest Point)
L = Length of conductor (ft) | 122
n = 1, 1.5,2.25 | 1.5
D = Sideflash (ft) | 13.5556
Notes:
L = length of lightning protection conductor between its grounded point and the point under consideration (closest to roof)
n = 1 where there is a single overhead conductor that exceeds 200 ft in horizontal length
n = 1.5 where there is a single overhead wire or more than one wire interconnected above the structure to be protected, such that only two down conductors are located greater than 20 ft and less then 100 ft apart
n = 2.25 where there are more than two down conductors spaced more than 25 ft apart within a 100-ft wide area that are interconnected above the structure being protected
SIDEFLASH - At Highest Point of Building | Metal Parts (Guard Rails) | Metal Parts (Air Ventilator)
h - Height of Protected Structure (ft): | 23.6667 | 7
D = Sideflash (D=h/6) (ft): | 3.9444 | 1.1667
Notes: h - Height of the structure or object requiring protection