## Data Sheet
U.S. Army Corps of Engineers
Air Leakage Rate by Fan Pressurization
Using ASTM E 779-10
Building Name | [8 empty] | Test Date
Building Address
Prime Contractor
Contract No.
Pressure Testing Agency
Testing Agency Address
Testing Agency Contact | [7 empty] | Phone
Lead On-Site Personnel | [7 empty] | Phone
Witness Name |  |  | Organization |  |  | Telephone |  |  | Email
Building / Test Comments
What method is used for this pressure test? | [6 empty] | Blower Door | [10 empty] | Pressure Test Requirements |  |  | Army | Navy | AF | This Test
[7 empty] | Trailer Mounted Fan | [6 empty] | 1 | Equipment type |  |  | Number of Pre Test Bias Pressure Data Points |  |  | 12 | 12 | 12 | 12
[7 empty] | Building Air Handling System | [10 empty] | Number of Pressure Test Data Points |  |  | 10 | 10 | 10 | 10
[18 empty] | Number of Post-test Bias Pressure Data Points |  |  | 12 | 12 | 12 | 12
Is this an Air Force, Army or Navy Building? | [6 empty] | Army | [10 empty] | Maximum Allowable Bias Pressure (Pa) |  |  | NA | NA | NA | NA
[7 empty] | Navy | [6 empty] | 3 | DoD Branch |  |  | Minumum Test Pressure (Pa) - Double Sided |  |  | 40 | 40 | 25 | 25
[7 empty] | Air Force | [10 empty] | Minumum Test Pressure (Pa) - Single sided |  |  | 50 | 50 | 25 | 25
[18 empty] | Lowest Allowable Maximum Test Pressure (Pa) |  |  | 75 | 75 | 50 | 50
Note: Performing a two-sided test is highly recommended for increased result accuracy. | [17 empty] | Test Pressure Range (Pa) |  |  | 25 | 25 | 25 | 25
[18 empty] | Data Correlation Coefficient |  |  | 0.98 | 0.98 | 0.98 | 0.98
What type of test is being performed? | [6 empty] | Positive & Negative - Two Sided | [10 empty] | Acceptable Leakage Rate (cfm/ft2) |  |  | 0.25 | 0.25 | 0.4 | 0.4
[7 empty] | Positive - Single Sided | [6 empty] | 1 | Test Type |  |  | Maximum Bias Pressure (Pa) - % of Min Test Two sided |  |  | 30% | 30% | 30% | 30%
[7 empty] | Negative - Single Sided | [10 empty] | Maximum Bias Pressure (Pa) - % of Min Test One sided |  |  | 30% | 30% | 30% | 30%
[18 empty] | Allowable 95% Confidence Interval (CI) |  |  | 0.02 | 0.02 | 0.02 | 0.02
Building Data
Elevation Above Sea Level (ft) |  |  |  | 760 |  | Building Envelope Pressure (Pa) |  |  |  |  | 75
Envelope Surface Area (ft2) |  |  |  | 80000 |  | Acceptable Leakage Rate (cfm/ft2) |  |  |  |  | 0.25
Test Conditions
Indoor Temperature (oF) |  |  | Outdoor Temperature (oF) |  |  |  |  | Average Wind Speed (MPH) |  |  |  | 5
Pre Test |  | 75.2 | Pre Test |  |  |  | 62.6 | Prevailing Wind Direction |  |  |  | W
Post Test |  | 75.2 | Post Test |  |  |  | 62.6 | Average Bias Pressure (Pa) |  |  |  | -0.3
Average |  | 75.2 | Average |  |  |  | 62.6
Pre Test Bias Pressure Test Points
Pressure (Pa) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| -0.4 | -0.4 | -0.4 | -0.4 | -0.4 | -0.4 | -0.4 | -0.4 | -0.4 | -0.4 | -0.4 | -0.4
Post Test Bias Pressure Test Points
Pressure (Pa) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| -0.2 | -0.2 | -0.2 | -0.2 | -0.2 | -0.2 | -0.2 | -0.2 | -0.2 | -0.2 | -0.2 | -0.2
CALCULATION TABLES
Positive Pressure Test Data | [12 empty] | Enter all pressure data as positve values.
Pressure (Pa) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  |  |  |  | Positive Pressure Test
| 40.9 | 45.1 | 50.5 | 55.6 | 61.7 | 65.1 | 67.7 | 71.1 | 74.3 | 81.6 |  |  |  |  | Bias & Temp -Corrected
Fan 1 | 11022 | 12230 | 13144 | 14022 | 15054 | 15596 | 16002 | 16541 | 17022 | 18207 |  |  |  |  | Pressure | Leakage |  |  | ρo= | 0.07517
Fan 2 | [14 empty] | (Pa) | (cfm) | Ln(ΔP) | Ln(Q) | ρin = | 0.07218
Fan 3 | [13 empty] | 1 | 41.2 | 11382.7823 | 3.7184 | 9.3399 | ρout = | 0.07392
Fan 4 | [13 empty] | 2 | 45.4 | 12630.3237 | 3.8155 | 9.4439 | µo = | 0.043892
Fan 5 | [13 empty] | 3 | 50.8 | 13574.2416 | 3.9279 | 9.5159 | µin = | 0.044353
Fan 6 | [13 empty] | 4 | 55.9 | 14480.9811 | 4.0236 | 9.5806 | µout = | 0.043544
Fan 7 | [13 empty] | 5 | 62 | 15546.7615 | 4.1271 | 9.6516 | C = | 847.7057
Fan 8 | [13 empty] | 6 | 65.4 | 16106.5027 | 4.1805 | 9.687 | N= | 10
Fan 9 | [13 empty] | 7 | 68 | 16525.7923 | 4.2195 | 9.7127
Fan 10 | [13 empty] | 8 | 71.4 | 17082.4353 | 4.2683 | 9.7458 | S2ln(dP) = | 0.050016
Fan 11 | [13 empty] | 9 | 74.6 | 17579.1799 | 4.3121 | 9.7745 | S2ln(Q) = | 0.024884
Fan 12 | [13 empty] | 10 | 81.9 | 18802.9684 | 4.4055 | 9.8418 | Sln(dP)ln(Q) = | 0.035218
Gauge (cfm) | 11022 | 12230 | 13144 | 14022 | 15054 | 15596 | 16002 | 16541 | 17022 | 18207 | 0 | 0 |  | 11 | 0.3 | 0 | NA | NA | Sn = | 0.065811
Actual (cfm) | 11114.802 | 12332.973 | 13254.6686 | 14140.0611 | 15180.7503 | 15727.3137 | 16136.7321 | 16680.2704 | 17165.3202 | 18360.2976 | 0.01 | 0.01 |  | 12 | 0.3 | 0 | NA | NA | Sln(Q)(ln(dPr)) = | 0.020003
[19 empty] | T = | 2.306
Positive Pressure Test - Data Quality Check | [18 empty] | Iln(Q)(ln(dP)) = | 0.046126
Number of Pre Test Bias Pressure Data Points | 5: 12; 6: PASS; 7: 12 Points Required
Number of Pressure Test Data Points | 5: 10; 6: PASS; 7: 10 Points Required
Number of Post Test Bias Pressure Data Points | 5: 12; 6: PASS; 7: 12 Points Required
Maximum Bias Pressure (Pa) | 5: 0.4; 6: PASS; 7: For a two-sided test, the maximum allowable bias pressure is 30 percent of the lowest pressure data point - 12.27 Pa
Minumum Test Pressure (Pa) | 5: 40.9; 6: PASS; 7: For an Air Force, single sided, test the lowest allowable data point pressure is 25 Pa
Lowest Allowable Maximum Pressure Data Point (Pa) | 5: 81.6; 6: PASS; 7: The lowest allowable maximum pressure data point is 50 Pa
Test Pressure Range (Pa) | 5: 40.7; 6: PASS; 7: Must be > 25 Pa
Data Correlation Coefficient (r) Squared | 5: 0.99652; 6: PASS; 7: Must be > 0.98
Negative Pressure Test Data | [12 empty] | Enter all pressure data as positve values. | [7 empty] | Combined Positive and Negative Tests
Pressure (Pa) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  |  |  |  | Negative Pressure Test
| 42.2 | 46.9 | 50.8 | 54.7 | 59.3 | 64.4 | 68.7 | 72.5 | 77.4 | 82.1 |  |  |  |  | Bias & Temp -Corrected | [5 empty] | Combined Positive and Negative Tests | ρo= | 0.07517
Fan 1 | 10424 | 11242 | 12076 | 12452 | 13229 | 14106 | 14837 | 15397 | 16166 | 17067 |  |  |  |  | Pressure | Leakage |  |  | ρo= | 0.07517 |  | ρ = | 0.07305
Fan 2 | [14 empty] | (Pa) | (cfm) | Ln(ΔP) | Ln(Q) | ρin = | 0.07218 |  | µo = | 0.043892
Fan 3 | [13 empty] | 1 | 41.9 | 10387.2929 | 3.7353 | 9.2483 | ρout = | 0.07392 |  | µ = | 0.043949
Fan 4 | [13 empty] | 2 | 46.6 | 11202.4124 | 3.8416 | 9.3239 | µo = | 0.043892 |  | C = | 763.654
Fan 5 | [13 empty] | 3 | 50.5 | 12033.4755 | 3.922 | 9.3954 | µin = | 0.044353 |  | n= | 0.71513
Fan 6 | [13 empty] | 4 | 54.4 | 12408.1515 | 3.9964 | 9.4261 | µout = | 0.043544 |  | N= | 20
Fan 7 | [13 empty] | 5 | 59 | 13182.4153 | 4.0775 | 9.4866 | C = | 691.8916 |  | S2ln(dP) = | 0.047215
Fan 8 | [13 empty] | 6 | 64.1 | 14056.3271 | 4.1604 | 9.5508 | N= | 10 |  | Sn = | 0.066835
Fan 9 | [13 empty] | 7 | 68.4 | 14784.7529 | 4.2254 | 9.6014 |  |  |  | Sln(Q)(ln(dPr)) = | 0.034279
Fan 10 | [13 empty] | 8 | 72.2 | 15342.7809 | 4.2794 | 9.6384 | S2ln(dP) = | 0.04966 |  | T = | 2.1009
Fan 11 | [13 empty] | 9 | 77.1 | 16109.073 | 4.3451 | 9.6871 | S2ln(Q) = | 0.026136 |  | Iln(Q)(ln(dP)) = | 0.072017
Fan 12 | [13 empty] | 10 | 81.8 | 17006.9002 | 4.4043 | 9.7414 | Sln(dP)ln(Q) = | 0.035991
Gauge (cfm) | 10424 | 11242 | 12076 | 12452 | 13229 | 14106 | 14837 | 15397 | 16166 | 17067 | 0 | 0 |  | 11 | -0.3 | 0 | NA | NA | Sn = | 0.05131
Actual (cfm) | 10637.7328 | 11472.505 | 12323.6052 | 12707.3147 | 13500.2462 | 14395.2282 | 15141.2165 | 15712.6987 | 16497.4662 | 17416.9403 | 0.01 | 0.01 |  | 12 | -0.3 | 0 | NA | NA | SLn(Q)(ln(dPr)) = | 0.015609
[19 empty] | T = | 2.306
Negative Pressure Test - Data Quality Check | [18 empty] | Iln(Q)(ln(dP)) = | 0.035995
Number of Pre Test Bias Pressure Data Points | 5: 12; 6: PASS; 7: 12 Points Required
Number of Pressure Test Data Points | 5: 10; 6: PASS; 7: 10 Points Required
Number of Post Test Bias Pressure Data Points | 5: 12; 6: PASS; 7: 12 Points Required
Maximum Bias Pressure (Pa) | 5: 0.4; 6: PASS; 7: For a two-sided test, the maximum allowable bias pressure is 30 percent of the lowest pressure data point - 12.66 Pa.
Minumum Test Pressure Data Point (Pa) | 5: 42.2; 6: PASS; 7: For a two-sided test, the lowest allowable data point pressure is 25 Pa
Lowest Allowable Maximum Pressure Data Point (Pa) | 5: 82.1; 6: PASS; 7: The lowest allowable maximum pressure data point is 50 Pa
Test Pressure Range (Pa) | 5: 39.9; 6: PASS; 7: Must be > 25 Pa
Data Correlation Coefficient (r) Squared | 5: 0.99801; 6: PASS; 7: Must be > 0.98
Calculated Values | 7: Positive Test; 9: Negative Test; 11: Pos & Neg Test
Effective Leakage Area (AL) @ 75 Pa (ft2) | 7: 13.3562; 9: 11.9104; 11: 12.6333
Pressure Exponent, n | 7: 0.70413; 9: 0.72474; 11: 0.71443
Air Leakage Coefficient - CCorr (cfm/Pan) | 7: 841.1689; 9: 686.2452; 11: 763.707
Leakage Rates @ 75 Pa (Q75) (cfm)
Envelope Leakage Rate | 7: 17585.9845; 9: 15682.3706; 11: 16634.1775
Upper 95% Confidence Leakage Rate | 7: 18416.1588; 9: 16257.1387; 11: 17830.9295
Lower 95% Confidence Leakage Rate | 7: 16793.2333; 9: 15127.9232; 11: 15466.2976
Leakage per square foot of envelope area @ 75 Pa (cfm/ft2)
Leakage per Sq. Ft. of Envelope | 7: 0.21982; 9: 0.19603; 11: 0.20793
Upper 95% Confidence Limit | 7: 0.2302; 9: 0.20321; 11: 0.22289
Lower 95% Confidence Limit | 7: 0.20992; 9: 0.1891; 11: 0.19333
95% Confidence Interval (CI) | 7: 0.010377; 9: 0.0071846; 11: 0.014959
Pressure Test Results | 7: Positive Test; 9: Negative Test; 11: Pos & Neg Test
0.45 < Exponent (n) < 0.8 | 7: PASS; 9: PASS; 11: NA
Envelope Leakage Rate < 0.25 cfm/sq ft | 7: PASS; 9: PASS; 11: PASS
Upper 95% Confidence Limit < 0.27 cfm/sq ft | 7: PASS; 9: PASS; 11: NA
The envelope leakage rate is less than 0.25 cfm/sq ft and the 95% confidence interval is less than 0.02 OR The envelope leakage rate is less than 0.25 cfm/sq ft, the 95% confidence interval is greater than 0.02 and the leakage rate plus the 95% confidence interval is less than 0.25 cfm/sq ft. | 7: PASS; 9: PASS; 11: NA
[16 empty] | Pressure | Leakage
[16 empty] | (Pa) | (cfm)
[16 empty] | 75 | 20000
| Positive Test Correction Factor |  |  |  | 1.0084
| Pressure | Flow
| 40.9 | 11114.802 | 3.7111 | 9.316
| 45.1 | 12332.973 | 3.8089 | 9.42
| 50.5 | 13254.6686 | 3.922 | 9.4921 | P | This area is used for calculating the combined slope and interceprt for the actual fan flow and uncorrected data and plotting the combined trendline
| 55.6 | 14140.0611 | 4.0182 | 9.5568 | O
| 61.7 | 15180.7503 | 4.1223 | 9.6278 | S
| 65.1 | 15727.3137 | 4.1759 | 9.6632 | I
| 67.7 | 16136.7321 | 4.2151 | 9.6889 | T
| 71.1 | 16680.2704 | 4.2641 | 9.722 | I
| 74.3 | 17165.3202 | 4.3081 | 9.7506 | V
| 81.6 | 18360.2976 | 4.4018 | 9.8179 | E |  | Uncorrected Data Set Slope and Intercept
| NA | NA | NA | NA |  |  | Combined |  | Positive |  | Negative
| NA | NA | NA | NA |  |  | n = | 0.71446 | n = | 0.70043 | n = | 0.72849
| 42.2 | 10637.7328 | 3.7424 | 9.2722 |  |  | C = | 769.2963 | C = | 843.3918 | C = | 695.2007
| 46.9 | 11472.505 | 3.848 | 9.3477
| 50.8 | 12323.6052 | 3.9279 | 9.4193 | N |  | Combined
| 54.7 | 12707.3147 | 4.0019 | 9.4499 | E |  | Trendline
| 59.3 | 13500.2462 | 4.0826 | 9.5105 | G |  | P | Q
| 64.4 | 14395.2282 | 4.1651 | 9.5747 | A |  | 35 | 9755.9157
| 68.7 | 15141.2165 | 4.2297 | 9.6252 | T |  | 100 | 20654.4224
| 72.5 | 15712.6987 | 4.2836 | 9.6622 | I |  | 20 | 20
| 77.4 | 16497.4662 | 4.349 | 9.711 | V
| 82.1 | 17416.9403 | 4.4079 | 9.7652 | E |  | 75 | Pa
| NA | NA | NA | NA |  |  | Line
| NA | NA | NA | NA |  |  | 75 | 100
| Pressure | Flow |  |  |  |  | 75 | 20654.4224
| Negative Test Correction Factor |  |  |  | 1.0205
Note on A76: Actual Airflow at site conditions (elevation and temperature)
Note on A105: Actual Airflow at site conditions (elevation and temperature)

## Sheet1 (2)
x | y | Calculated | Percent
N-2 | T | T | Error
3 | 3.182 | 3.1789 | 0.09622%
4 | 2.776 | 2.7854 | -0.3393%
5 | 2.571 | 2.5657 | 0.206%
6 | 2.447 | 2.4415 | 0.2261%
7 | 2.365 | 2.365 | -0.0002745%
8 | 2.306 | 2.3104 | -0.1898%
9 | 2.262 | 2.266 | -0.1747%
10 | 2.228 | 2.2284 | -0.01683%
11 | 2.201 | 2.1979 | 0.1411%
12 | 2.179 | 2.1751 | 0.1782%
13 | 2.16 | 2.1591 | 0.0402%
14 | 2.145 | 2.1471 | -0.09627%
15 | 2.131 | 2.135 | -0.1878%
16 | 2.12 | 2.1203 | -0.01502%
17 | 2.11 | 2.1054 | 0.2172%
18 | 2.101 | 2.1028 | -0.08781%
| 6 | 1.9406e-06
| 5 | -0.00013776
| 4 | 0.0039822
| 3 | -0.060159
| 2 | 0.50555
| 1 | -2.3023
| C | 6.8696