|  |
| --- |
| **Title:** Glass Break Sensor - ContactType |
| **Objective:** Verify device is installed using acceptable standards and practices, communicates properly with the IDS, and provides proper protection of assets and meets or exceeds the contract performance specification. |
| **Applicability:** Glass Break Sensors (Contact Type) |
| **Notes:**   1. Real-time voice communications between the workstation operator and the field technician is required. 2. The field technician may need tools and a stepladder to perform the test. 3. Conduct the intrusion test with a lightweight tool such as the plastic handle of a screwdriver. 4. Perform all tests with the associated zone in the ACCESS state. 5. If multiple sensors are used to protect an alarmed zone, disable all sensors except the unit being tested. Restore all sensors to normal operation following the completion of testing. 6. Line Supervision, Power Fail, and Tamper Tests need to be performed in addition to these procedures. |

| **Steps** | **Actions** | **Expected Results** |
| --- | --- | --- |
| **1.0** | **Intrusion Test** |  |
|  |  |  |
| 1.1 | Lightly rap the glass in the corner farthest from the sensor. | An intrusion alarm is received at the workstation. |
|  |  |  |
| 1.2 | Clear the intrusion alarm at the workstation. | The active alarm queue is empty. |
|  |  |  |