SECTION 01513 - TEMPORARY PRESSURE DIFFERENTIAL AND AIR CIRCULATION SYSTEM

TEMPORARY PRESSURE DIFFERENTIAL AND AIR CIRCULATION SYSTEMS ARE DESCRIBED BY OSHA AS NEGATIVE PRESSURE ENCLOSURES. THESE SYSTEMS ARE USUALLY SIMPLE TO SET UP ONCE SOME BASIC PRINCIPLES ARE UNDERSTOOD. HOWEVER, THESE CAN BECOME COMPLEX IN HIGH-RISE BUILDINGS AND IF THERE ARE ACTIVE HVAC SYSTEMS INVOLVED OR MACHINERY SUCH AS ELEVATORS. REFER TO THE EVALUATIONS FOR DISCUSSION ON THIS TOPIC.

PART 1 - GENERAL

1.1	RELATED DOCUMENTS:

A.	Drawings and general provisions of Contract, including General and Supplementary Conditions and other Division-1 Specification Sections, apply to work of this section.

1.2	RELATED SECTIONS

DELETE THE FOLLOWING IF THERE ARE NO REQUIREMENTS SET FORTH IN SECTION 01503

A.	Heating and cooling requirements are set forth in Section 01503 Temporary Facilities - Asbestos Abatement.

BELOW MAY BE MORE APPROPRIATE IN THE PART OF SECTION 01013 "SUMMARY OF WORK - ASBESTOS ABATEMENT THAT DESCRIBES THE OWNERS MONITORING OF THE PROJECT. THE EQUIPMENT NECESSARY FOR THIS IS GENERALLY AVAILABLE FROM ASBESTOS ABATEMENT EQUIPMENT SUPPLIERS.

1.3	MONITORING

A.	Continuously monitor and record the pressure differential between the Work Area and the building outside of the Work Area with a monitoring device incorporating a continuous recorder (e.g. strip chart).

1.4	SUBMITTALS

A.	Before Start of Work:  Submit design of pressure differential system to the  Designer for review.  Do not begin work until submittal is returned with the  Designer's action stamp indicating that the submittal is returned for unrestricted use.  Include in the submittal at a minimum:

1.	Number of HEPA filtered fan units required and the calculations necessary to determine the number of machines

2.	Description of projected air flow within Work Area and methods required to provide adequate air flow in all portions of the work area

3.	Anticipated pressure differential across Work Area enclosures

4.	Description of methods of testing for correct air flow and pressure differentials

5.	Manufacturer's product data on the HEPA filtered fan units to be used

6.	Location of the machines in the Work Area

7.	Method of supplying adequate power to the machines and designation of building electrical panel(s) which will be supplying the power.

8.	Description of work practices to insure that airborne fibers travel away from workers

9.	Manufacturer's product data on equipment used to monitor pressure differential between inside and outside of Work Area.

INCLUDE THE NEXT THREE PARAGRAPHS IF AN AUXILIARY POWER SUPPLY FOR THE HEPA FILTERED FAN UNITS IS TO BE PROVIDED.

10.	Manufacturer's product data on auxiliary generator to be used

11.	Manufacturer's product data on auxiliary power switch to be used

12.	Schematic diagram of power and auxiliary power supply to  HEPA filtered fan units

B.	On a weekly basis:  Submit printout from pressure differential monitoring equipment.  Mark printout with date and start of time for each day.  Use printout paper that indicates elapsed time in intervals no greater than hours.  Indicate on each days record times of starting and stopping abatement work, type of work in progress, breaks for lunch or other purposes, periods of stop work, and filter changes.  Cut printout into segments by day, attach to 8 " by 11" [ 215 X 280 mm ]  paper.  Label with project name, contractors name and date.

1.5	QUALITY ASSURANCE:

ADD ADDITIONAL MONITORING POSITIONS SUCH AS AT CRITICAL OCCUPIED ADJACENT AREAS.

A.	Monitor pressure differential at Personnel and Equipment Decontamination Units with a differential pressure meter equipped with a continuous recorder.  Meter shall be equipped with a warning buzzer which will sound if pressure differential drops below 0.02 inch [ 0.5 mm ] of water.

PART 2 - PRODUCTS

2.1	HEPA FILTERED FAN UNITS:

A.	General:  Supply the required number of HEPA filtered fan units to the site in accordance with these specifications.  Use units that meet the following requirements.

B.	Cabinet:  Constructed of durable materials able to withstand damage from rough handling and transportation.  The width of the cabinet should be less than 30 inches [ 0.76 meters ] to fit through standard-size doorways.  Provide units whose cabinets are:

1.	Factory-sealed to prevent asbestos-containing dust from being released during use, transport, or maintenance

2.	Arranged to provide access to and replacement of all air filters from intake end

3.	Mounted on casters or wheels

C.	Fans:  Rate capacity of fan according to usable air-moving capacity under actual operating conditions.

D.	HEPA Filters:  Provide units whose final filter is the HEPA type with the filter media (folded into closely  pleated panels) completely sealed on all edges with a  structurally rigid frame.

1.	Provide units with a continuous rubber gasket located between the filter and the filter housing to form a tight seal.

2.	Provide HEPA filters that are individually  tested and certified by the manufacturer to have  an efficiency of not less than 99.97 percent when challenged with  0.3 um dioctylphthalate (DOP) particles when tested in accordance with Military Standard Number 282 and Army  Instruction Manual 136-300-175A.  Provide filters that bear a UL586 label to indicate ability to perform under specified conditions.

3.	Provide filters that are marked with: the name of the manufacturer, serial number, air flow rating, efficiency and resistance, and the direction of test air flow.

ULTRA HIGH EFFICIENCY AIR (ULPA) FILTERS WITH 99.99% EFFICIENCY ARE AVAILABLE. DEPENDING UPON AVAILABILITY, REVISE THE ABOVE TO THIS MORE STRINGENT STANDARD FOR CRITICAL AREAS.

4.	Pre-filters, which protect the final filter by removing the larger particles, are required to prolong the operating life of the HEPA filter.  Two stages of pre-filtration are required.  Provide units with the following pre-filters:

a.	First-stage pre-filter: low-efficiency type (e.g., for particles 100 um and larger)

b.	Second-stage (or intermediate) filter:  medium efficiency (eg., effective for particles down to 5 um)

c.	Provide units with pre-filters and intermediate filters installed either on or in the intake grid of the unit and held in place with special housings or clamps.

E.	Instrumentation:   Provide units equipped with:

1.	Magnehelic gauge or manometer to measure the pressure drop across filters and indicate when filters have become loaded and need to be changed

2.	A table indicating the usable air-handling capacity for various static pressure readings on the Magnehelic gauge affixed near the gauge for reference, or the Magnehelic reading indicating at what point the filters should be changed, noting Cubic Feet per Minute (CFM) (Liters / Second (LPS)) air delivery at that point

3.	Elapsed time meter to show the total accumulated hours of operation

F.	Safety and Warning Devices:  Provide units with the following safety and warning devices:

1.	Electrical (or mechanical) lockout to prevent fan from operating without a HEPA filter

2.	Automatic shutdown system to stop fan in the event of a rupture in the HEPA filter or blocked air discharge

3.	Warning lights to indicate normal operation (green), too high a pressure drop across the filters (i.e., filter overloading) (yellow), and too low of a pressure drop (i.e., rupture in HEPA filter or obstructed discharge) (red)

4.	Audible alarm if unit shuts down due to operation of safety systems

G.	Electrical components:  Provide units with electrical components approved by the National Electrical Manufacturers Association (NEMA) and Underwriter's Laboratories (UL).  Each unit is to be equipped with overload protection sized for the equipment.  The motor, fan, fan housing, and cabinet are to be grounded.

H.	Manufacturers:  Subject to compliance with requirements, manufacturers offering products which may be incorporated in the work include, but are not limited to, the following:

RETAIN ABOVE OR BELOW, FOR NONPROPRIETARY OR SEMI-PROPRIETARY SPECIFICATION. ABOVE IS THE CURRENT REPLACEMENT FOR THE FORMER "OR EQUAL" CLAUSE.

I.	Manufacturer:  Subject to compliance with requirements, provide products of the following:

EDIT THE FOLLOWING LIST AS REQUIRED FOR PROJECT REQUIREMENTS.

1.	HEPA filtered Fan Units:  The following machines are standard 2000 CFM machines used in typical asbestos abatement jobs.

Aerospace America, Inc.		"Aero-Clean 2000"

900 Truman Parkway

P.O. Box 189

Bay City, Michigan  48707

(517) 684-2121

Abatement Technologies		"HEPA-AIRE 1990 and HEPA-AIRE 2000"

3305 Breckinridge Blvd. #118

Deluth, GA 30136

(800) 634-9091 or (404) 925-2761

Global Consumer Services, Inc.

4615-1U E. Industrial St.

Sims Valley, CA  93063

(805) 579-0230

M-Tec Corp.				Micro-Trap

1300 W. Steel Rd.				Alumina II

Unit #2

Morrisville, PA  19067

(215) 295-8208

2.	Large Capacity:  The following are large capacity 5000-6000 CFM machines used on large asbestos abatement jobs.

Abatement Technologies			"HEPA-AIRE 5000"

3305 Breckinridge Blvd. #118		model H5000C

Deluth, GA 30136

(800) 634-9091 or (404) 925-2761

3.	Hazardous Locations:  The following are pneumatically powered machines for use in asbestos abatement jobs in hazardous locations where electric motors are prohibited.

Abatement Technologies			"HEPA-AIRE PNEUMATIC"

3305 Breckinridge Blvd. #118		model H2000P

Deluth, GA 30136

(800) 634-9091 or (404) 925-2761

INCLUDE THE FOLLOWING TWO PARAGRAPHS IF AN AUXILIARY POWER SUPPLY FOR THE HEPA FILTERED FAN UNITS IS TO BE PROVIDED.

DELETE IF NO AUXILIARY GENERATOR IS TO BE USED.

2.2	AUXILIARY GENERATOR:

A.	Auxiliary Generator:  Provide a gasoline-powered self-starting generator with a capacity adequate to power a minimum of 50% of the HEPA filtered fan units in operation at any time during the work.

2.3	AUXILIARY POWER SWITCH:

A.	Auxiliary Power Switch:  Provide a switching relay which will automatically start auxiliary generator and switch over power supplied to HEPA filtered fan units to auxiliary generator.

PART 3 - EXECUTION

AUGMENTING THE PHYSICAL BARRIER BY MAINTAINING THE WORK AREA AT AN AIR PRESSURE LOWER THAN SURROUNDING SPACES IS THE ONLY EFFECTIVE METHOD OF INSURING ISOLATION. ACCOMPLISHING THIS REQUIRES MORE THAN MERELY INSTALLING SOME PORTABLE HEPA FILTERED FAN UNITS. REFER TO EVALUATIONS FOR MORE INFORMATION ON THE DESIGN OF PRESSURE DIFFERENTIAL ISOLATION SYSTEMS.

THE FOLLOWING PARAGRAPHS OFFER EXAMPLES OF LANGUAGE APPLICABLE TO A NUMBER OF SITUATIONS BUT ARE NOT A COMPLETE TREATMENT OF WHAT CAN BE A COMPLEX ENGINEERING PROBLEM. IN HIGH RISE BUILDINGS OR OTHER COMPLEX STRUCTURES A PROFESSIONAL MECHANICAL ENGINEER OR OTHER PROFESSIONAL SKILLED IN THE DESIGN OF HVAC SYSTEMS SHOULD BE CONSULTED.

3.1	PRESSURE DIFFERENTIAL ISOLATION

A.	Isolate the Work Area from all adjacent areas or systems of the building with a Pressure Differential that will cause a movement of air from outside to inside at any breach in the physical isolation of the Work Area.

B.	Relative Pressure in Work Area:  Continuously maintain the work area at an air pressure that is lower than that in any surrounding space in the building, or at any location in the immediate proximity outside of the building envelope. This pressure differential when measured across any physical or critical barrier must equal or exceed a static pressure of:

CHOOSE ONE OF THE FOLLOWING AND DELETE THE REST. REFER TO THE EVALUATIONS FOR A DISCUSSION ON THE SELECTION OF A PRESSURE DIFFERENTIAL.

FOLLOWING IS THE MINIMUM REQUIRED BY OSHA.

1.	0.02 inches (0 .5 mm ) of water.

THE FOLLOWING IS THE MAXIMUM PRESSURE DIFFERENTIAL IT IS PRACTICAL TO MAINTAIN WITHOUT SPECIAL PRACTICES. REFER TO EVALUATIONS.

2.	0.03 inches (0.75 mm ) of water.

THE FOLLOWING SHOULD BE ADEQUATE TO ISOLATE A WORK AREA IN A ONE STORY BUILDING WHERE WIND VELOCITIES ARE NOT EXPECTED TO EXCEED 25 MILES PER HOUR, OR A 5 STORY BUILDING WHERE WIND VELOCITIES ARE NOT EXPECTED TO EXCEED 15 MILES PER HOUR. REFER TO EVALUATIONS.

3.	0.04 inches ( 1 mm ) of water.

THE FOLLOWING IS ALLOWED FOR BUILDING OVER FOUR STORIES BY THE STATE OF NEW JERSEY IF SPECIAL SEALS ARE USED (N.J.A.C. 5:23-8.19(C). REFER TO EVALUATIONS.

4.	0.05 inches ( 1.27 mm ) of water.

FOLLOWING IS AN UPPER LIMIT ON THE PRESSURE DIFFERENTIAL POSSIBLE TO DEVELOP. PRESSURES DIFFERENTIALS AT THIS LEVEL COULD DEVELOP LATERAL FORCES HIGH ENOUGH TO CAUSE DAMAGE TO WALLS OR OTHER BUILDING ELEMENTS. ACHIEVING THIS LEVEL WILL REQUIRE SPECIFIC AND DETAILED DESIGN OF ENCLOSURES SYSTEMS. UNLESS THERE ARE EXTENUATING CIRCUMSTANCES IT IS GENERALLY PREFERABLE TO USE A MORE MODERATE PRESSURE DIFFERENTIAL AND LOCAL ISOLATION AS DESCRIBED BELOW. REFER TO EVALUATIONS FOR ADDITIONAL DISCUSSION.

5.	0.10 inches ( 2.5 mm)  of water.

THE NUMBER OF UNITS THAT MUST BE EXHAUSTED IS DEPENDENT ON HOW LEAK TIGHT THE WORK AREA IS. THE FOLLOWING SETS OUT THE GROUND RULES FOR THE EMPIRICAL DETERMINATION OF THE REQUIRED NUMBER OF FANS. REFER TO EVALUATIONS FOR MORE DISCUSSION.

C.	Accomplish the pressure differential by exhausting a sufficient number of HEPA filtered fan units from the work area.  The number of units required will depend on machine characteristics, the seal at barriers, and required air circulation. The number of units will increase with increased make-up air or leaks into the Work Area.  Determine the number of units required for pressure isolation by the following procedure:

1.	Establish required air circulation in the work area, personnel and equipment decontamination units.

2.	Establish isolation by increased pressure in adjacent areas or as part of seals where required.

3.	Exhaust a sufficient number of units from the work area to develop the required pressure differential.

4.	The required number of units is the number determined above plus one additional unit.

CHOOSE ONE OF THE TWO PARAGRAPHS BELOW. GENERALLY RETAIN FOLLOWING AS A PREFERABLE PROCEDURE.

5.	Vent HEPA filtered fan units to outside of building unless authorized in writing by  Designer.

FOLLOWING SHOULD ONLY BE USED WHERE IT IS NOT FEASIBLE TO EXHAUST TO THE BUILDING EXTERIOR. EDIT FOR PROJECT SPECIFICS. THE CONTROLLED AREA SHOULD BE SPECIFICALLY LOCATED EITHER ON THE DRAWINGS OR BELOW. THE SECOND UNIT PROVIDES ADDITIONAL PROTECTION AGAINST A HEPA FILTER FAILURE. VERIFY WITH MANUFACTURERS OF EQUIPMENT TO BE USED THAT THIS ARRANGEMENT WILL NOT RESULT IN PREMATURE EQUIPMENT FAILURE OR OTHER PRACTICAL PROBLEM.

6.	Vent each HEPA filtered fan unit to inlet of second unit.  Vent second unit to a controlled area in the building.  Insure that controlled area is isolated from balance of building by critical barriers at all times that units are in operation.

ALWAYS RETAIN FOLLOWING PARAGRAPHS DESCRIBING DUCTING.

7.	Mount units to exhaust directly or through disposable ductwork.

THE FOLLOWING INSURES THAT DUCTWORK USED PREVIOUSLY ON THE INTAKE (CONTAMINATED SIDE) WILL NOT BE USED.

8.	Use only new ductwork except for sheet metal connections and elbows.

9.	Use ductwork and fittings of same diameter or larger than discharge connection on fan unit.

10.	Use inflatable, disposable plastic ductwork in lengths not greater than 100 feet (30 meters).

11.	Use spiral wire-reinforced flex duct in lengths not greater than 50 feet (15 meters).

12.	Arrange exhaust as required to inflate duct to a rigidity sufficient to prevent flapping.

13.	If direction of discharge from fan unit is not aligned with duct use sheet metal elbow to change direction.  Use six feet ( 2 meters) of spiral wire reinforced flex duct after direction change.

FOLLOWING IS A MINIMUM. ON LARGE PROJECTS DISCUSS REQUIREMENTS WITH ELEVATOR DESIGN AND BUILDING ENGINEERS. COORDINATE THIS WITH LIMITATIONS ON USE OF ELEVATORS IN SECTION 01013 "SUMMARY OF WORK - ASBESTOS ABATEMENT." EDIT BELOW TO AVOID DUPLICATION OR CONFLICT WITH REQUIREMENTS OF SECTION 01526 - TEMPORARY ENCLOSURES. REFER TO THE EVALUATIONS FOR DISCUSSION.

D.	Isolation of elevators, stair towers, and return air intakes:  Erect seals with an air space at doors to elevators and stair towers.  Pressurize this space with HEPA-filtered air so that it is at a pressure greater than either the Work Area elevator shaft or stair tower.

SELECT ONE OF THE PARAGRAPHS BELOW AND DELETE THE OTHER.

FOLLOWING IS NON-COMBUSTIBLE CONSTRUCTION AND SHOULD BE USED WHERE FIRE SAFETY IS A CONCERN OR WHERE REQUIRED BY LOCAL BUILDING OR FIRE CODES. IF THIS SECTION IS USED A SECTION ON GYPSUM DRYWALL SHOULD BE INCLUDED.

1.	Fabricate seal by first sealing door with duct tape and 6 mil polyethylene.  Construct a barrier from " (13 mm) gypsum board supported by 3-5/8" (92 mm) x 25 gauge metal studs at 16" (410 mm) on centers.  Space face of barrier a minimum of 3" (76 mm)  from face of door.  Seal barrier with 6 mil (0.15 mm) sheet plastic and duct tape.

USE FOLLOWING WHERE SMALL AREAS ARE INVOLVED OR LOCATIONS SUCH AS SINGLE STORY BUILDINGS WHERE FIRE RESISTANCE IS LESS CRITICAL.

2.	Fabricate seal by first sealing door with duct tape and 6 mil (0.15 mm) polyethylene.  Construct a barrier from " (13mm) CDX plywood supported by 2" X 4" (51 mm x 102 mm) wood studs at 16" (410 mm) on centers.  Space face of barrier a minimum of 3" (76 mm) from face of door.  Seal barrier with 6 mil (0.15 mm) sheet plastic and duct tape.

3.	Use plywood and framing lumber that is treated to be fire resistant.

THE PRESSURE DIFFERENTIAL INDICATED BELOW MAY HAVE TO BE CHANGED DEPENDING UPON THE LOW AIR FLOW SHUT DOWN SETTING OF THE PARTICULAR HEPA FILTERED FAN UNIT USED. CONSULT UNIT MANUFACTURER FOR SPECIFIC INFORMATION.

4.	Pressurize space with exhaust from HEPA filtered fan unit.  Continuously maintain a pressure differential with this space a minimum of 0.02 inches (0.5 mm) of water higher in static pressure than any adjacent space.

5.	Locate HEPA filtered fan unit outside of work area.  Fabricate a manifold as required to distribute air to individual spaces to be isolated.  Provide relief venting at unit as required to prevent shut down due to low air flow while still maintaining required air pressure.

ISOLATION OF CHASES AND ENCLOSED STAIRS CAN FREQUENTLY BE ACCOMPLISHED BY PRESSURIZING THE SPACE RATHER THAN ERECTING A PRESSURIZED SEAL AS ABOVE. THE PARTICULAR METHOD USED SHOULD BE DETERMINED DURING PROJECT DESIGN. REFER TO THE EVALUATIONS FOR MORE DISCUSSION.

E.	Isolation of chases and enclosed stairs:  Pressurize chases and enclosed stairs with HEPA filtered air so that it is at a pressure greater than any adjacent work area.

1.	Pressurize space with exhaust from HEPA filtered fan unit.  Continuously maintain a pressure differential with this space a minimum of 0.02 (.5 mm ) inches of water higher in static pressure than any adjacent work area.

FOLLOWING PARAGRAPH SHOULD BE USED WHERE PRESSURIZING AIR IS TAKEN FROM OUTSIDE OR FROM TEM-CLEARED PORTIONS OF THE BUILDING. THIS IS A LOW RISE BUILDING PROCEDURE. PRESSURIZATION OF SHAFTS IS DIFFICULT IN HIGH RISE BUILDING.

F.	Isolation of chases and enclosed stairs:  Pressurize chases and enclosed stairs so that they are at a pressure greater than any adjacent work area.

1.	Pressurize space with centrifugal-type fans.  Axial type fans are not to be used for this purpose.  Continuously maintain a pressure differential in this space a minimum of 0.02 inches ( 0.5 mm)  of water higher in static pressure than any adjacent work area.

THE PREFERABLE METHOD OF ISOLATION IS TO ARRANGE THE WORK AREA SO THAT RETURN AIR DUCTWORK IS OUTSIDE AND NOT IMMEDIATELY ADJACENT TO THE WORK AREA. ANY DUCT RUNNING THROUGH THE WORK AREA THAT LEADS TO OPERATING HVAC EQUIPMENT SHOULD, IF POSSIBLE, BE PHYSICALLY CUT AT THE WORK AREA BARRIERS.

IF A RETURN AIR DUCT IN THE WORK AREA MUST REMAIN IN OPERATION IT SHOULD BE ISOLATED AS DESCRIBED BELOW.

G.	Isolation of return air ductwork:  Return air duct work which must be kept operating is located in the Work Area.  This duct work is to be isolated from the Work Area by an enclosure forming an annular space around the duct which is positively pressurized with HEPA filtered air.

1.	Wrap the duct with 6 mil (0.15 mm) polyethylene.  Seal all polyethylene seams with spray glue and duct tape.

2.	Enclose wrapped duct with two layers of polyethylene.  Fabricate inner layer from 6 mil  (0.15 mm) polyethylene with all seams sealed with spray glue and duct tape.  Arrange outer layer to support inner layer.  Fabricate out of reinforced sheet plastic with seams sealed with spray glue and duct tape and reinforced with staples.  Support outer layer with a frame work fabricated from 2" x 4"s (51 mm x 102 mm) at 24" (610 mm) on center.  Enclosures less than 2'-6' in diameter may be reinforced with box strapping in lieu of wood framing.

FOLLOWING SHOULD BE USED WHEREVER ABATEMENT WORK IS BEING CARRIED OUT IN AN OCCUPIED BUILDING.

DELETE THE FOLLOWING IF AN AUXILIARY GENERATOR IS NOT TO BE USED.

3.2	AUXILIARY GENERATOR

A.	Provide auxiliary gasoline-powered generator located outside of the building in a location protected from the weather.  Install the generator in a location so that the exhaust from the generator does not flow to any building ventilation or supplied air intakes.  Arrange so that if a power failure occurs the generator automatically starts and supplies power to a minimum of 50% of the HEPA filtered fan units in operation.

3.3	AIR CIRCULATION IN THE WORK AREA:

A.	Air Circulation:  For purposes of this section air circulation refers to either the introduction of outside air to the Work Area or the circulation and cleaning of air within the Work Area.

B.	Air circulation in the Work Area is a minimum requirement intended to help maintain airborne fiber counts at a level that does not significantly challenge the work area isolation measures.  The Contractor may also use this air circulation as part of the engineering controls in  the worker protection program.

C.	Determining the Air circulation Requirements:  The air flow volume (cubic meters per minute) exhausted (removed) from the workplace must exceed the amount of makeup air supplied to the enclosure. Provide a fully operational air circulation system supplying a minimum of the following air circulation rate:

FOLLOWING IS A MINIMUM REQUIREMENT BY OSHA ADEQUATE ONLY WHERE THE WORK IS EXPECTED TO GENERATE LOW AIRBORNE FIBER LEVELS. REFER TO EVALUATIONS FOR DISCUSSION ON DETERMINING AIR CIRCULATION REQUIREMENTS.

1.	4 air changes per hour

FOLLOWING IS USED WHERE ABATEMENT WORK IS EXPECTED TO RAISE HIGHER AIRBORNE FIBER LEVELS. REMOVAL OF CHRYSOTILE-CONTAINING SURFACE TREATMENTS IS A TYPICAL EXAMPLE OF THIS WORK.

2.	12 air changes per hour

FOLLOWING IS APPROPRIATE WHERE HIGH AIRBORNE FIBER COUNTS ARE EXPECTED. DRY REMOVAL OF CHRYSOTILE CONTAINING INSTALLATIONS, REMOVAL OF AMOSITE OR CROCIDOLITE-CONTAINING MATERIALS ARE EXAMPLES OF THIS TYPE OF WORK.

3.	20 air changes per hour

D.	Determine Number of Units needed to achieve required air circulation according to the following procedure:

1.	Determine the volume in cubic feet of the work area by multiplying floor area by ceiling height.  Determine total air circulation requirement in cubic feet per minute (CFM) for the work area by dividing this volume  by 60 and multiplying by the air change rate.

2.	Air Circulation Required in Cubic Feet of Air per Minute (CFM) =

Volume of work area (cu. ft.)     X  Number of air changes per hour

60 (minutes per hour)

DELETE ABOVE OR BELOW. BELOW IS THE CALCULATION FOR METRIC UNITS

3.	Determine the volume in cubic meters of the work area by multiplying floor area by ceiling height.  Determine total air circulation requirement in cubic feet per minute  liters / second  (LPS) for the work area by dividing this volume by 3.6 and multiplying by the air change rate.

4.	Air Circulation Required in Liters / second=

Volume of work area (cubic meters)     	  X  Number of air changes per hour

3.6

5.	Divide the air circulation requirement (CFM) (( LPS))  above by capacity of HEPA filtered fan unit(s) used.  Capacity of a unit for purposes of this section is the capacity in cubic feet per minute (Liters  / second) with fully loaded filters (pressure differential which causes loaded filter warning light to come on) in the machine's labeled operating characteristics.

6	Number of Units Needed =

Air circulation Requirement (CFM) ((LPS))

Capacity of Unit with Loaded Filters (CFM) ((LPS))

7	Add one (1) additional unit as a backup in case of equipment failure or machine shutdown for filter changing.

FOLLOWING LANGUAGE SHOULD BE USED IF AN EXHAUST SYSTEM IS TO BE USED. DELETE IF A RECIRCULATION SYSTEM IS TO BE USED. THE FOLLOWING SECTIONS COULD BE REVISED TO PERMIT THE CONTRACTOR THE OPTION OF EITHER SYSTEM.

FOLLOWING IS ESSENTIALLY THE ARRANGEMENT DESCRIBED AS A "NEGATIVE PRESSURE SYSTEM" PATENTED BY ANTHONY NATALE. SEE EVALUATIONS.

3.4	EXHAUST SYSTEM:

A0	Pressure differential isolation and air circulation and pressure differential in the Work Area are to be accomplished by an exhaust system as described below.

1	Exhaust all units from the Work Area to meet air circulation requirement of this section.

2	Location of HEPA Filtered Fan Units:   Locate fan unit(s) so that makeup air enters work area primarily through decontamination facilities and traverses Work Area as much as possible.  This may be accomplished by positioning the HEPA filtered fan unit(s) at a maximum distance from the worker access opening or other makeup air sources.

PREFERABLY THE LOCATION OF FAN UNITS AND MAKEUP AIR SOURCES SHOULD BE SHOWN ON DRAWINGS. A MINIMUM PRACTICE IS TO LOCATE THESE ITEMS AT PRECONSTRUCTION MEETING.

3	The end of the unit or its exhaust duct should be placed through an opening in the plastic barrier or wall covering.  Seal plastic around the unit or duct with tape.

4	Vent to Outside of Building, unless authorized in writing by the Designer.

5	Air Handling Unit Exhaust:  The exhaust plume from air handling units should be located away from adjacent personnel and intakes for HVAC systems.

THIS MAY INVOLVE THE USE OF ADDITIONAL LENGTHS OF FLEXIBLE OR RIGID DUCT CONNECTED TO THE AIR OUTLET AND ROUTED TO THE NEAREST OUTSIDE OPENING. WINDOW PANES WHICH HAVE TO BE REMOVED TEMPORARILY SHALL BE REINSTALLED AT THE COMPLETION OF THE WORK.

6	Decontamination Units:  Arrange Work Area and decontamination units so that the majority of make up air comes through the Decontamination Units.  Use only personnel or equipment Decontamination Unit at any time and seal the other so that make up air passes through unit in use.

7	Supplemental Makeup Air Inlets:  Provide where required for proper air flow through the Work Area in location approved by the  Designer by making openings in the plastic sheeting that allow air from outside the building into the Work Area.  Locate auxiliary makeup air inlets as far as possible from the fan unit(s) (e.g., on an opposite wall), off the floor (preferably near the ceiling), and away from barriers that separate the Work Area from occupied clean areas.  Cover with flaps to reseal automatically if the pressure differential system should shut down for any reason.  Spray flap and around opening with spray adhesive so that if flap closes meeting surfaces are both covered with adhesive.  Use adhesive that forms contact bond when dry.

FOLLOWING LANGUAGE SHOULD BE USE IF A RECIRCULATION SYSTEM IS TO BE USED. DELETE IF AN EXHAUST SYSTEM IS TO BE USED. THIS IS ESSENTIALLY THE ARRANGEMENT KNOWN AS THE PRESSURE DIFFERENTIAL CONTAINMENT SYSTEM DEVELOPED BY THE BRAND COMPANY, A LARGE ASBESTOS ABATEMENT CONTRACTING FIRM, AS AN ALTERNATIVE TO THE NEGATIVE AIR SYSTEM PATENTED BY ANTHONY NATALE.

3.5	RECIRCULATION SYSTEM:

A0	Pressure differential isolation and air circulation in the Work Area are to be accomplished by a recirculation system as described below.

1	Recirculate air in the Work Area through HEPA filtered fan units to accomplish air circulation requirements of this section.

2	Location of Fan Units:  Locate HEPA filtered fan units so that air is circulated through all parts of the Work Area, and so that required pressure is maintained at all parts of Work Area geometry.  Move units as necessary, so that in any location where asbestos-containing materials are being disturbed,  air movement is directed away from employees , and toward the HEPA filter fan unit.  Direct air flow in these locations so that it is predominantly toward workers' backs at the breathing zone elevation.

3.6	AIR CIRCULATION IN DECONTAMINATION UNITS:

IT IS CRITICAL TO WORKER SAFETY THAT THERE BE A SENSIBLE MOVEMENT OF AIR THROUGH THE DECONTAMINATION UNIT FROM THE CLEAN SIDE OF THE SHOWER TOWARD THE WORK AREA. THIS MOVEMENT OF AIR MUST BE ADEQUATE TO CARRY AWAY AIRBORNE FIBERS THAT RESULT FROM THE DECONTAMINATION AND SHOWERING PROCESS SO THAT THE WORKER IS BREATHING CLEAN AIR WHEN THE RESPIRATOR IS REMOVED. THIS WILL TYPICALLY RESULT IN A DRAFTY SHOWER BUT A SAFE WORKER.

A0	Pressure Differential Isolation:  Continuously maintain the pressure differential required for the work area in the:

1	Personnel Decontamination Unit:  across the Shower Room with the Equipment Room at a lower pressure than the Clean room.

2	Equipment Decontamination Unit:  Across the Holding Room with the Wash Room at a lower pressure than the Clean Room.

B0	Air Circulation:  Continuously maintain air circulation in Decontamination Units at same level as required for Work Area.

C0	Air Movement:  Arrange air circulation through the Personnel Decontamination Unit so that it produces a movement of air from the Clean Room through the Shower Room into the Equipment Room.   At each opening, the air flow velocity must be sufficient to provide visible indications of air movement into the work area..  The velocity of air flow within the enclosure must be adequate to remove airborne contamination from each worker's breathing zone without disturbing the asbestos-containing material on surfaces.

3.7	USE OF THE PRESSURE DIFFERENTIAL AND AIR CIRCULATION SYSTEM:

EDIT TO MATCH REQUIREMENTS OF SPECIFIC MACHINE SPECIFIED.

A0	General:  Each unit shall be serviced by a dedicated minimum  115V-20A circuit with ground fault circuit interrupter (GFCI) supplied from temporary power supply installed under requirements of Section 01503 "Temporary Facilities."  Do not use existing branch circuits to power fan units.

B0	Air Flow Tests:  Air flow patterns will be checked before removal operations begin, at least once per operating shift and any time there is a question regarding the integrity of the enclosure.  The primary test for air flow is to trace air currents with smoke tubes or other visual methods.  Flow checks are made at each opening and at each doorway to demonstrate that air is being drawn into the enclosure and at each worker's position to show that air is being drawn away from the workers location and toward the HEPA filtration unit.

C0	Demonstrate Condition of Equipment for each HEPA filtered fan unit and pressure differential monitoring equipment including proper operation of the following:

1	Squareness of HEPA Filter

2	Condition of Seals

3	Proper operation of all lights

4	Proper operation of automatic shut down if exhaust is blocked

5	Proper operation of alarms

6	Proper operation of Magnehelic gauge

7	Proper operation and calibration on pressure monitoring equipment

D0	Demonstrate Operation of the pressure differential system to the  Designer will include, but not be limited to, the following:

1	Plastic barriers and sheeting move lightly in toward Work Area,

2	Curtain of decontamination units move lightly in toward Work Area,

3	There is a noticeable movement of air through the Decontamination Unit.

4	Use smoke tube to demonstrate air movement from Clean Room through Shower Room to Equipment Room.

5	Use smoke tubes to demonstrate a definite motion of air across all areas in which work is to be performed.

IT MAY BE MORE PRACTICAL FOR THE PROJECT ADMINISTRATOR TO CONDUCT THE TEST BELOW.

6	Use a differential pressure meter or manometer to demonstrate the required pressure differential at every barrier separating the Work Area from the balance of the building, equipment, ductwork or outside.

7	Modify the Pressure Differential System as necessary to demonstrate successfully the above.

E0	Use of System During Abatement Operations:

1	Start fan units before beginning work (before any asbestos-containing material is disturbed).  After abatement work has begun, run units continuously to maintain a constant pressure differential and air circulation until decontamination of the work area is complete.  Do not turn off units at the end of the work shift or when abatement operations temporarily stop.

2	Monitoring Pressure Within the Enclosure:  After the initial air flow patterns have been checked, the static pressure must be monitored within the enclosure.  Monitoring may be made using manometers, pressure gauges, or combinations of these devices.  It is recommended that they be attached to alarms and strip chart recorders

3	Do not shut down air  pressure differential system during encapsulating procedures, unless authorized by the  Designer in writing.  Supply sufficient pre-filters to allow frequent changes.

4	Start abatement work at a location farthest from the fan units and proceed toward them.  If an electric power failure occurs, immediately stop all abatement work and do not resume until power is restored and fan units are operating again.

5	Corrective Actions:  If the manometers or pressure gauges demonstrate a reduction in pressure differential below the required level, work should cease and the reason for the  change investigated and appropriate changes made.  The air flow patterns should be retested before work begins again.

6	At completion of abatement work, allow fan units to run as specified under section 01711, to remove airborne fibers that may have been generated during abatement work and cleanup and to purge the Work Area with clean makeup air.  The units may be required to run for a longer time after decontamination, if dry or only partially wetted asbestos material was encountered during any abatement work.

F0	Dismantling the System:

1	When a final inspection and the results of final air tests indicate that the area has been decontaminated, fan units may be removed from the Work Area.  Before removal from the Work Area, remove and properly dispose of pre-filter, decontaminate exterior of machine and seal intake to the machine with 6 mil (0.15 mm) polyethylene to prevent environmental contamination from the filters.

END OF SECTION  - 01513